## Cover
Your HVAC Co. | HVAC PM Checklist
HVAC PREVENTIVE MAINTENANCE CHECKLIST
📋 SERVICE CALL INFORMATION
Work Order #: | Technician Name:
Service Date: | Technician License #:
Next Service Due: | Company:
Service Type: | Supervisor / Lead:
Priority: | Customer PO #:
Call-In / Request By: | Time On Site:
🏢 SITE & EQUIPMENT INFORMATION
Site / Facility Name: | Manufacturer:
Site Address: | Model Number:
Building / Area: | Serial Number:
Floor / Zone: | Install Year:
Unit / System Tag: | Equipment Age (yrs):
Equipment Type: | Warranty Status:
🌡️ SERVICE CONDITIONS
Outdoor Temp (°F): | Unit Mode (Cool/Heat/Fan):
Indoor Temp (°F): | Runtime Hours (if metered):
Outdoor RH (%): | Last Service Date:
Indoor RH (%): | Last Filter Change:
Weather Conditions: | Control System Type:
✅ TECHNICIAN SIGN-OFF
Technician: | Signature:
Reviewed By: | Date Completed:
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## AHU Checklist
Your HVAC Co. |  |  |  |  | HVAC PM Checklist
🏭 AIR HANDLING UNIT (AHU) — PM CHECKLIST
Inspection / Task Item | Pass | Fail | N/A | Measurement / Reading | Notes / Corrective Action
▶ FILTERS
Inspect filter condition — check for loading, damage, bypass | ☐ | ☐ | ☐
Record filter static pressure drop (in. wg) | ☐ | ☐ | ☐
Replace filters per schedule — note MERV rating installed | ☐ | ☐ | ☐
Verify filter media is seated, no bypass around frame | ☐ | ☐ | ☐
Check filter rack/housing — clean if needed | ☐ | ☐ | ☐
Document new filter P/N, MERV rating, and quantity installed | ☐ | ☐ | ☐
▶ FAN & MOTOR
Inspect fan wheel / blades — clean, no debris or damage | ☐ | ☐ | ☐
Check fan shaft bearings — listen for noise, check for heat | ☐ | ☐ | ☐
Lubricate fan shaft bearings (if not sealed) | ☐ | ☐ | ☐
Measure motor amp draw (all phases) — record vs FLA | ☐ | ☐ | ☐
Measure motor voltage (all phases) — check for imbalance | ☐ | ☐ | ☐
Check motor mount bolts — tighten if loose | ☐ | ☐ | ☐
Inspect motor windings — check for overheating, odor | ☐ | ☐ | ☐
Check VFD operation and parameter settings (if installed) | ☐ | ☐ | ☐
Verify fan rotation direction is correct | ☐ | ☐ | ☐
▶ DRIVE / BELTS / SHEAVES
Inspect drive belts — check for cracking, glazing, fraying | ☐ | ☐ | ☐
Check belt tension — adjust to spec | ☐ | ☐ | ☐
Check belt alignment — realign sheaves if needed | ☐ | ☐ | ☐
Inspect sheave condition — no cracks, wear grooves | ☐ | ☐ | ☐
Record belt size and quantity | ☐ | ☐ | ☐
Lubricate drive components as required | ☐ | ☐ | ☐
▶ COILS & HEAT EXCHANGE
Inspect evaporator / cooling coil — clean fins, no frost | ☐ | ☐ | ☐
Clean coil if fouling >10% — document method used | ☐ | ☐ | ☐
Inspect heating coil — no damage, scale, or fouling | ☐ | ☐ | ☐
Check coil connections for leaks — refrigerant or hydronic | ☐ | ☐ | ☐
Measure coil entering / leaving air temp (DB) | ☐ | ☐ | ☐
Measure coil entering / leaving air temp (WB) — cooling only | ☐ | ☐ | ☐
▶ DRAIN PAN & CONDENSATE
Inspect drain pan — clean, no standing water or algae | ☐ | ☐ | ☐
Flush and test condensate drain line — confirm free flow | ☐ | ☐ | ☐
Prime condensate trap (if equipped) | ☐ | ☐ | ☐
Check condensate pump operation — test float switch (if installed) | ☐ | ☐ | ☐
Inspect drain pan insulation — no deterioration | ☐ | ☐ | ☐
▶ DAMPERS & CONTROLS
Inspect outside air damper — clean, full range of motion | ☐ | ☐ | ☐
Inspect return air damper — check blade seals and linkage | ☐ | ☐ | ☐
Inspect mixed air / economizer damper operation | ☐ | ☐ | ☐
Calibrate damper actuators — verify position feedback | ☐ | ☐ | ☐
Check thermostat / sensor setpoints — document | ☐ | ☐ | ☐
Test smoke detector / fire/smoke damper (if equipped) | ☐ | ☐ | ☐
Verify BAS/DDC points are reading correctly | ☐ | ☐ | ☐
▶ CABINET & GENERAL
Inspect unit cabinet — no corrosion, loose panels, or gaps | ☐ | ☐ | ☐
Check all access door gaskets — replace if deteriorated | ☐ | ☐ | ☐
Clean unit interior — remove dust, debris | ☐ | ☐ | ☐
Inspect flexible duct connections — no tears or separations | ☐ | ☐ | ☐
Check vibration isolators — springs floating, no contact | ☐ | ☐ | ☐
Verify unit labeling / tagging is legible | ☐ | ☐ | ☐
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## RTU Checklist
Your HVAC Co. |  |  |  |  | HVAC PM Checklist
🌬️ ROOFTOP UNIT (RTU) / PACKAGED UNIT — PM CHECKLIST
Inspection / Task Item | Pass | Fail | N/A | Measurement / Reading | Notes / Corrective Action
▶ CABINET & UNIT EXTERIOR
Inspect unit cabinet — no corrosion, dents, or missing panels | ☐ | ☐ | ☐
Inspect roof curb and flashing — no leaks or deterioration | ☐ | ☐ | ☐
Check all access panels — hinges, latches, and seals intact | ☐ | ☐ | ☐
Inspect unit base and structural members for rust / damage | ☐ | ☐ | ☐
Verify unit is level — check vibration isolators | ☐ | ☐ | ☐
Clean unit exterior — remove debris from top and around unit | ☐ | ☐ | ☐
▶ FILTERS
Inspect filter condition — note loading and bypassing | ☐ | ☐ | ☐
Record filter differential pressure (in. wg) | ☐ | ☐ | ☐
Replace filters — document MERV, size, and quantity | ☐ | ☐ | ☐
Verify filter rack seal — no air bypass | ☐ | ☐ | ☐
▶ SUPPLY / RETURN FAN SECTION
Inspect supply fan wheel / blades — clean, balanced | ☐ | ☐ | ☐
Check fan shaft bearings — noise, vibration, heat | ☐ | ☐ | ☐
Lubricate bearings (if applicable) | ☐ | ☐ | ☐
Measure supply fan motor amps (all phases) | ☐ | ☐ | ☐
Measure supply fan motor voltage (all phases) | ☐ | ☐ | ☐
Inspect drive belts — tension, alignment, condition | ☐ | ☐ | ☐
Check VFD operation and fault log (if installed) | ☐ | ☐ | ☐
▶ COOLING SYSTEM — DX
Measure suction line pressure / temperature | ☐ | ☐ | ☐
Measure discharge line pressure / temperature | ☐ | ☐ | ☐
Calculate superheat (suction) — record vs target | ☐ | ☐ | ☐
Calculate subcooling (liquid) — record vs target | ☐ | ☐ | ☐
Check refrigerant charge — no signs of loss or leak | ☐ | ☐ | ☐
Inspect compressor — unusual noise, vibration, or heat | ☐ | ☐ | ☐
Measure compressor amp draw (all phases) | ☐ | ☐ | ☐
Check compressor contactor — contacts, coil, overload | ☐ | ☐ | ☐
Inspect condenser coil — clean fins, no damage | ☐ | ☐ | ☐
Clean condenser coil if fouling present | ☐ | ☐ | ☐
Inspect condenser fan blades and motor — check amps | ☐ | ☐ | ☐
Test crankcase heater (if equipped) | ☐ | ☐ | ☐
Check high and low pressure controls / safeties | ☐ | ☐ | ☐
Inspect TXV / EXV operation (if accessible) | ☐ | ☐ | ☐
▶ HEATING SECTION
Inspect heat exchanger / burner — no cracks, corrosion | ☐ | ☐ | ☐
Check burner ignition — spark, glow plug, or pilot | ☐ | ☐ | ☐
Inspect flue/vent connection — no blockage or gaps | ☐ | ☐ | ☐
Measure supply air temperature in heat mode | ☐ | ☐ | ☐
Test limit switch, high-temp cutout, and rollout switch | ☐ | ☐ | ☐
Inspect gas valve and manifold — no leaks | ☐ | ☐ | ☐
Check heat strips (electric heat) — amp draw vs nameplate | ☐ | ☐ | ☐
▶ CONTROLS & SAFETIES
Test thermostat / building controller setpoints | ☐ | ☐ | ☐
Verify economizer operation — controls and damper position | ☐ | ☐ | ☐
Test smoke detector / fire damper (if equipped) | ☐ | ☐ | ☐
Check all safeties — operation and set points | ☐ | ☐ | ☐
Inspect wiring — no loose terminals or chafed insulation | ☐ | ☐ | ☐
Check contactor contacts — pitting, burning | ☐ | ☐ | ☐
Test defrost cycle (heat pump units only) | ☐ | ☐ | ☐
▶ DRAIN PAN & CONDENSATE
Inspect drain pan — no algae, standing water, or cracks | ☐ | ☐ | ☐
Flush and test condensate drain — confirm free flow | ☐ | ☐ | ☐
Check condensate pump (if installed) | ☐ | ☐ | ☐
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Refrigeration Data
Your HVAC Co. |  |  |  |  | HVAC PM Checklist
❄️ REFRIGERATION SYSTEM — DX DATA & READINGS
Parameter | Design / Target | Measured Value | Unit | Tolerance | Status | Notes
Refrigerant Type |  |  |  | —
System Operating Mode |  |  |  | —
Suction Pressure |  |  | PSIG | Per Mfr
Discharge Pressure |  |  | PSIG | Per Mfr
Suction Saturation Temp (SST) |  |  | °F | Per Mfr
Discharge Saturation Temp (DST) |  |  | °F | Per Mfr
Suction Line Temp |  |  | °F | Per Mfr
Superheat (Suction) |  |  | °F | 8–12°F
Liquid Line Temp |  |  | °F | Per Mfr
Subcooling (Liquid) |  |  | °F | 10–15°F
Compressor Discharge Temp |  |  | °F | <225°F
Outdoor Ambient Temp (DB) |  |  | °F | —
Indoor Return Air Temp (DB) |  |  | °F | —
Indoor Return Air Temp (WB) |  |  | °F | —
Indoor Supply Air Temp (DB) |  |  | °F | —
Indoor Supply Air Temp (WB) |  |  | °F | —
Evaporator Coil Delta-T (DB) |  |  | °F | 15–20°F
Condenser Coil Approach Temp |  |  | °F | 10–20°F
Compressor Amps — L1 |  |  | Amps | <FLA
Compressor Amps — L2 |  |  | Amps | <FLA
Compressor Amps — L3 |  |  | Amps | <FLA
Condenser Fan Amps |  |  | Amps | <FLA
Evaporator Fan Amps |  |  | Amps | <FLA
Supply Voltage L1–L2 |  |  | Volts | ±5%
Supply Voltage L2–L3 |  |  | Volts | ±5%
Supply Voltage L1–L3 |  |  | Volts | ±5%
📊 REFRIGERANT CHARGE SUMMARY
Refrigerant Added (lbs):
Refrigerant Recovered (lbs):
Reason for Adjustment:
Recovery Cylinder #:
EPA 608 License #:
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Electrical & Controls
Your HVAC Co. |  |  |  |  | HVAC PM Checklist
⚡ ELECTRICAL & CONTROLS — PM DATA SHEET
Parameter | Nameplate / Design | Measured Value | Unit | Status | Notes
Supply Voltage L1–L2 |  |  | Volts | ±5%
Supply Voltage L2–L3 |  |  | Volts | ±5%
Supply Voltage L1–L3 |  |  | Volts | ±5%
Voltage Imbalance (%) |  |  | % | <2%
Supply Fan Motor FLA (Nameplate) |  |  | Amps | —
Supply Fan Amps — L1 |  |  | Amps | <FLA
Supply Fan Amps — L2 |  |  | Amps | <FLA
Supply Fan Amps — L3 |  |  | Amps | <FLA
Condenser Fan FLA (Nameplate) |  |  | Amps | —
Condenser Fan Amps |  |  | Amps | <FLA
Compressor FLA (Nameplate) |  |  | Amps | —
Compressor Amps — L1 |  |  | Amps | <FLA
Compressor Amps — L2 |  |  | Amps | <FLA
Compressor Amps — L3 |  |  | Amps | <FLA
Heating Element #1 Amps (if elec.) |  |  | Amps | <FLA
Heating Element #2 Amps (if elec.) |  |  | Amps | <FLA
Control Circuit Voltage |  |  | Volts | ±10%
Ground Fault Protection — Tested |  |  |  | Pass/Fail
Motor Insulation Resistance (MΩ) |  |  | MΩ | >1 MΩ
🎛️ CONTROLS & THERMOSTAT VERIFICATION
Control Item | Setpoint / Design | As-Found | As-Left | Status | Notes
Cooling Setpoint (°F)
Heating Setpoint (°F)
Deadband / Differential (°F)
Supply Air Setpoint (°F)
Economizer Changeover Setpoint
OSA Minimum Position (%)
High Pressure Cutout (PSIG)
Low Pressure Cutout (PSIG)
Freeze Stat Setpoint (°F)
Smoke Detector Setpoint
Fan Proven Switch — Tested
Defrost Termination Setpoint (HP)
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Hydronic Checklist
Your HVAC Co. |  |  |  |  | HVAC PM Checklist
💧 HYDRONIC / CHILLED WATER SYSTEM — PM CHECKLIST
Inspection / Task Item | Pass | Fail | N/A | Measurement / Reading | Notes / Corrective Action
▶ PUMPS
Inspect pump casing — no leaks, corrosion, or damage | ☐ | ☐ | ☐
Check pump shaft seal — no weeping or active leak | ☐ | ☐ | ☐
Lubricate pump bearings (if not sealed) | ☐ | ☐ | ☐
Measure pump motor amps (all phases) | ☐ | ☐ | ☐
Check impeller for cavitation noise or vibration | ☐ | ☐ | ☐
Verify pump rotation direction | ☐ | ☐ | ☐
Record suction and discharge pressure (in. wg or PSI) | ☐ | ☐ | ☐
Calculate pump differential pressure — compare to design | ☐ | ☐ | ☐
▶ CHILLER / BOILER (if applicable)
Inspect unit chassis — no leaks, corrosion, or damage | ☐ | ☐ | ☐
Check refrigerant / fluid charge (chiller) | ☐ | ☐ | ☐
Inspect burner and heat exchanger (boiler) | ☐ | ☐ | ☐
Record entering water temperature (EWT) | ☐ | ☐ | ☐
Record leaving water temperature (LWT) | ☐ | ☐ | ☐
Record system delta-T — compare to design | ☐ | ☐ | ☐
Inspect expansion tank — pressure and pre-charge correct | ☐ | ☐ | ☐
Check air separator / air vent — purge if needed | ☐ | ☐ | ☐
Check pressure relief valve — no weeping | ☐ | ☐ | ☐
▶ COILS & TERMINALS
Inspect fan coil units — clean coil fins and drain pan | ☐ | ☐ | ☐
Check coil connections — no leaks at unions or fittings | ☐ | ☐ | ☐
Verify control valve operation — full open/close | ☐ | ☐ | ☐
Check balancing valve position — record setting | ☐ | ☐ | ☐
Measure coil EWT and LWT | ☐ | ☐ | ☐
Inspect chilled beam operation (if installed) | ☐ | ☐ | ☐
▶ PIPING & SYSTEM
Check system pressure — compare to design operating range | ☐ | ☐ | ☐
Inspect all visible piping — no leaks, corrosion, or damage | ☐ | ☐ | ☐
Check pipe insulation integrity — no gaps or damage | ☐ | ☐ | ☐
Test glycol concentration (freeze protection %) — record | ☐ | ☐ | ☐
Inspect strainer basket — clean if clogged | ☐ | ☐ | ☐
Check system chemical treatment levels | ☐ | ☐ | ☐
Verify make-up water connection and backflow preventer | ☐ | ☐ | ☐
Inspect flexible connections — no cracks or separation | ☐ | ☐ | ☐
▶ CONTROLS & SAFETIES
Verify chilled water / heating water setpoints | ☐ | ☐ | ☐
Test flow switch / differential pressure switch | ☐ | ☐ | ☐
Check low-temperature freeze stat (if installed) | ☐ | ☐ | ☐
Verify pump proof of flow / VFD operation | ☐ | ☐ | ☐
Test building automation system (BAS) trend data | ☐ | ☐ | ☐
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Exhaust & Ventilation
Your HVAC Co. |  |  |  |  | HVAC PM Checklist
💨 EXHAUST & VENTILATION FAN — PM CHECKLIST
Inspection / Task Item | Pass | Fail | N/A | Measurement / Reading | Notes / Corrective Action
▶ FAN UNIT
Inspect fan housing — no cracks, corrosion, or damage | ☐ | ☐ | ☐
Inspect fan wheel / blades — clean, no damage or imbalance | ☐ | ☐ | ☐
Check fan shaft and bearing — listen for noise or heat | ☐ | ☐ | ☐
Lubricate bearings per manufacturer schedule | ☐ | ☐ | ☐
Check belt drive condition and tension (if belt-driven) | ☐ | ☐ | ☐
Verify fan rotates freely by hand (de-energized) | ☐ | ☐ | ☐
Measure fan amp draw — compare to nameplate FLA | ☐ | ☐ | ☐
Record fan CFM output — compare to design | ☐ | ☐ | ☐
▶ DUCTWORK & TERMINATIONS
Inspect inlet and discharge ductwork — no damage or blockage | ☐ | ☐ | ☐
Check duct connections at fan — no air leaks | ☐ | ☐ | ☐
Inspect flex connectors — no cracks or separation | ☐ | ☐ | ☐
Check exterior wall cap / roof cap — open freely, no damage | ☐ | ☐ | ☐
Verify damper operation — opens on call, closes at rest | ☐ | ☐ | ☐
Inspect bird/pest screens at terminations | ☐ | ☐ | ☐
▶ CONTROLS & SAFETIES
Test manual on/off operation at fan | ☐ | ☐ | ☐
Test occupancy sensor or timer control (if installed) | ☐ | ☐ | ☐
Test interlocks with AHU or make-up air unit | ☐ | ☐ | ☐
Verify speed control / VFD operation (if installed) | ☐ | ☐ | ☐
Check for fault codes on VFD or controller | ☐ | ☐ | ☐
Test smoke/fire damper interlocks (if equipped) | ☐ | ☐ | ☐
▶ BATHROOM / KITCHEN / LAB EXHAUST
Inspect grille / register at each exhaust terminal — clean | ☐ | ☐ | ☐
Measure exhaust CFM at each terminal (if balancing required) | ☐ | ☐ | ☐
Check kitchen hood capture velocity (if applicable) | ☐ | ☐ | ☐
Verify make-up air is adequate and balanced | ☐ | ☐ | ☐
Inspect grease filters (kitchen) — clean or replace | ☐ | ☐ | ☐
Check grease trap / duct for grease accumulation (kitchen) | ☐ | ☐ | ☐
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## PM Schedule
Your HVAC Co. | [6 empty] | HVAC PM Checklist
🗓️ PREVENTIVE MAINTENANCE SCHEDULE — ANNUAL TASK MATRIX
Maintenance Task | M | Q | SA | A | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep
LEGEND: M=Monthly Q=Quarterly SA=Semi-Annual A=Annual | M: ← Frequency; Jan: ← Check month completed (✓)
▶ FILTERS & AIR QUALITY
Inspect filter condition & differential pressure | bar: M
Replace standard filters (MERV 8) | bar: M to A
Replace high-efficiency filters (MERV 13+) | bar: Q
Clean filter racks and housing | bar: M to A
Test IAQ sensors — CO₂, humidity (if installed) | bar: SA
▶ FAN & MOTOR
Inspect belts, sheaves, and tension | bar: Q
Lubricate bearings (if non-sealed) | bar: M to A
Measure motor amps and voltage | bar: Q
Inspect motor mounting — tighten bolts | bar: M to A
Megger motor windings | bar: A
Check VFD fault log and parameters | bar: M to A
▶ REFRIGERATION / DX SYSTEM
Full DX refrigerant check — superheat / subcooling | bar: Q
Inspect compressor operation and amp draw | bar: M to A
Clean condenser coil | bar: SA
Clean evaporator coil | bar: M to A
Test high/low pressure safeties | bar: A
Leak check refrigerant circuit | bar: M to A
▶ ELECTRICAL & CONTROLS
Check and tighten all electrical connections | bar: SA
Test and verify all safety controls | bar: M to A
Calibrate thermostat / BAS sensors | bar: A
Test smoke detectors and fire dampers | bar: M to A
Inspect contactors and relays | bar: Q
▶ DRAIN PAN & CONDENSATE
Inspect and clean drain pan | bar: Q
Flush condensate drain line | bar: M to A
Test condensate pump operation | bar: Q
Prime condensate trap | bar: M to A
▶ HYDRONIC SYSTEM
Check system pressure and glycol concentration | bar: Q
Inspect pump seals and bearings | bar: M to A
Clean strainer baskets | bar: Q
Test chemical treatment levels | bar: M to A
Full pump and system inspection | bar: A
▶ DUCTWORK & AIRSIDE
Inspect visible ductwork for leaks or damage | bar: A
Check damper operation and linkages | bar: M to A
Measure and verify supply CFM at key terminals | bar: A
Clean exhaust fan grilles and registers | bar: M to A
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Parts & Materials Log
Your HVAC Co. |  |  |  |  | HVAC PM Checklist
🔩 PARTS, MATERIALS & CONSUMABLES LOG
# | Part / Material Name | Part Number / Description | Manufacturer | Qty | Unit | Unit Cost ($) | Total Cost ($) | Warranty? | Notes
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
TOTALS | [6 empty] | 0
💰 COST SUMMARY
Total Parts Cost ($): |  |  | 0
Labor Hours:
Labor Rate ($/hr):
Total Labor Cost ($):
Total Service Call Cost ($):
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Deficiency Log
Your HVAC Co. |  |  |  | HVAC PM Checklist
⚠️ DEFICIENCY LOG & CORRECTIVE ACTION TRACKING
# | Location / System | Deficiency Description | Corrective Action Required | Assigned To | Due Date | Date Resolved | Priority | Status
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
📊 DEFICIENCY SUMMARY
Total Deficiencies Identified: |  |  |  |  | 0
Open / Unresolved: |  |  |  |  | 0
Resolved / Closed: |  |  |  |  | 0
High Priority: |  |  |  |  | 0
Safety-Critical Items: |  |  |  |  | 0
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Summary & Sign-Off
Your HVAC Co. | [5 empty] | HVAC PM Checklist
HVAC PM CHECKLIST — SERVICE SUMMARY
📊 PM COMPLETION SUMMARY
PM Section | Items Checked | Pass | Fail | N/A | Completion % | Section Status
AHU / Air Handler
RTU / Packaged Unit
DX / Refrigeration System
Electrical & Controls
Hydronic / Chilled Water
Exhaust & Ventilation Fans
Filters & IAQ
Ductwork & Airside
📝 OVERALL FINDINGS & RECOMMENDATIONS
Overall PM Status:
Unit / System Condition:
Immediate Safety Concerns?:
Deficiencies Identified (Count):
Recommended Follow-Up Actions:
Estimated Equipment Remaining Life:
Next Scheduled PM Date:
🗒️ TECHNICIAN NARRATIVE & SERVICE NOTES
✍️ SIGN-OFF & ACCEPTANCE
Servicing Technician: |  |  | Print Name: |  |  | Signature: | Date:
EPA 608 License #: |  |  | Cert. Expiry: |  |  | Company: | Phone:
Supervisor / Lead Tech: |  |  | License #: |  |  | Signature: | Date:
Customer / Owner Rep: |  |  | Title: |  |  | Signature: | Date Accepted:
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com