## PPM Programme Cover
Your HVAC Co. | [5 empty] | HVAC PPM Checklist
PLANNED PREVENTIVE MAINTENANCE PROGRAMME
Scheduled HVAC Maintenance — Contract Document
📋 CONTRACT & PROGRAMME INFORMATION
PPM Contract #: | [5 empty] | Contract Start Date:
Contract Title: | [5 empty] | Contract End Date:
Contract Type (Full/Partial/Basic): | [5 empty] | Review / Renewal Date:
Contract Value (Annual): | [5 empty] | Programme Issue Date:
Client / Building Owner: | [5 empty] | Programme Revision #:
Client Contact Name: | [5 empty] | Prepared By:
Client Phone / Email: | [5 empty] | Authorised By:
🏢 SITE & FACILITY INFORMATION
Site / Facility Name: | [5 empty] | Site Reference Code:
Site Address — Line 1: | [5 empty] | City / State / Zip:
Building Type / Use: | [5 empty] | Total Gross Area (sq ft):
Number of Floors: | [5 empty] | Year Built:
Number of HVAC Systems: | [5 empty] | BMS / BAS System Type:
Site Access Contact: | [5 empty] | Emergency Contact:
Key Safe / Access Code Location: | [5 empty] | On-Site Safety Induction Required:
📅 PPM FREQUENCY LEGEND & SCOPE SUMMARY
W = Weekly FM = Fortnightly M = Monthly Q = Quarterly SA = Semi-Annual A = Annual BI = Biennial C = Condition-Based
Equipment Category | Asset Count | W | FM | M | Q | SA | A | BI | C | SLA Response | Included in Contract
Air Handling Units (AHU) | [9 empty] | 4 hrs | Yes | bar: M to A
Rooftop Units (RTU) | [9 empty] | 4 hrs | Yes | bar: W to C
Fan Coil Units (FCU) | [9 empty] | 8 hrs | Yes | bar: M; SA to A
Split / DX Systems | [9 empty] | 4 hrs | Yes | bar: W to C
Chillers | [9 empty] | 2 hrs | Yes | bar: M to BI
Cooling Towers | [9 empty] | 4 hrs | Yes | bar: W to C
Boilers / Hot Water | [9 empty] | 2 hrs | Yes | bar: M to A
Pumps (HVAC) | [9 empty] | 8 hrs | Yes | bar: Q to C
Exhaust / Ventilation Fans | [9 empty] | 8 hrs | Yes | bar: Q to A
BMS / Controls | [9 empty] | 4 hrs | Yes | bar: Q to C
Ductwork & Dampers | [9 empty] | 8 hrs | Yes | bar: SA to A; C
Refrigerant Systems | [9 empty] | 4 hrs | Yes | bar: Q to C
✍️ AUTHORISATION & SIGN-OFF
Service Provider Representative: |  | M: Signature:; BI: Date:
Client / Building Owner: |  | M: Signature:; BI: Date:
Contract Manager: |  | M: Signature:; BI: Date:
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Asset Register
Your HVAC Co. | [6 empty] | HVAC PPM Checklist
🗂️ HVAC ASSET REGISTER — EQUIPMENT INVENTORY
Asset ID | Asset Description | Location / Zone | Manufacturer | Model Number | Serial Number | Install Year | Rated Capacity | PPM Frequency | Last Service | Next Due | Condition | Warranty Exp. | Notes
HVAC-001
HVAC-002
HVAC-003
HVAC-004
HVAC-005
HVAC-006
HVAC-007
HVAC-008
HVAC-009
HVAC-010
HVAC-011
HVAC-012
HVAC-013
HVAC-014
HVAC-015
HVAC-016
HVAC-017
HVAC-018
HVAC-019
HVAC-020
HVAC-021
HVAC-022
HVAC-023
HVAC-024
HVAC-025
HVAC-026
HVAC-027
HVAC-028
HVAC-029
HVAC-030
📊 ASSET SUMMARY
Total Assets on Register: | [7 empty] | 30
Assets Requiring Immediate Attention: | [7 empty] | 0
Assets Under Warranty: | [7 empty] | 0
Assets Overdue for Service: | [7 empty] | 0
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Annual PPM Planner
Your HVAC Co. | [7 empty] | HVAC PPM Checklist
🗓️ ANNUAL PPM PLANNER — VISIT & TASK SCHEDULE
Asset / Task Description | Freq | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total Visits | Status
LEGEND: P = Planned C = Completed X = Missed / Overdue NA = Not Applicable ◑ = Part Complete
AHU-01 — Full Service (Filters, Belts, Coils) | [13 empty] | 4 | bar: Freq; Mar; Jun; Sep; Dec
AHU-01 — Filter Inspection | [13 empty] | 12 | bar: Freq to Dec
AHU-02 — Full Service | [13 empty] | 4 | bar: Freq; Mar; Jun; Sep; Dec
AHU-02 — Filter Inspection | [13 empty] | 12 | bar: Freq to Dec
RTU-01 — Full Service (Coils, DX, Electrics) | [13 empty] | 2 | bar: Freq; Jun; Dec
RTU-01 — Filter & Belt Check | [13 empty] | 4 | bar: Freq to Dec
RTU-02 — Full Service | [13 empty] | 2 | bar: Freq; Jun; Dec
RTU-02 — Filter & Belt Check | [13 empty] | 4 | bar: Freq to Dec
FCU Schedule — All Units (Filter Clean) | [13 empty] | 12 | bar: Freq to Dec
FCU Schedule — Coil & Valve Service | [13 empty] | 2 | bar: Freq to Dec
Chiller-01 — Full Annual Service | [13 empty] | 1 | bar: Freq; Jun
Chiller-01 — Monthly Condition Check | [13 empty] | 12 | bar: Freq to Dec
Cooling Tower — Water Treatment Check | [13 empty] | 12 | bar: Freq to Dec
Cooling Tower — Full Annual Clean | [13 empty] | 1 | bar: Freq to Dec
Boiler-01 — Full Annual Service + Gas Safe | [13 empty] | 1 | bar: Freq; Nov
Boiler-01 — Monthly Checks | [13 empty] | 12 | bar: Freq to Dec
HVAC Pump Schedule — All Pumps | [13 empty] | 4 | bar: Freq; Mar; Jun; Sep; Dec
Exhaust Fan Schedule — All Fans | [13 empty] | 2 | bar: Freq to Dec
BMS Annual Calibration & Trend Review | [13 empty] | 1 | bar: Freq; Jun
BMS Quarterly Point Check | [13 empty] | 4 | bar: Freq to Dec
Refrigerant Leak Check — All DX Systems | [13 empty] | 2 | bar: Freq; Jun; Dec
Damper & Fire Damper Annual Test | [13 empty] | 1 | bar: Freq to Dec
Emergency Lighting & Controls Test | [13 empty] | 2 | bar: Freq; Feb; Aug
Ductwork Inspection (Accessible Sections) | [13 empty] | 1 | bar: Freq to Dec
📊 ANNUAL PLANNER SUMMARY
Total Planned Visits: | Jan: 114
Total Completed: | bar: Freq to Jan
Completion Rate (%): | bar: Freq to Jan
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Monthly Visit Record
Your HVAC Co. | [5 empty] | HVAC PPM Checklist
📆 MONTHLY PPM VISIT RECORD — ATTENDANCE & TASK LOG
Asset / Task | Visit Month | Sched. Date | Actual Date | Technician | Time On | Time Off | Duration (hrs) | Tasks Completed | Defects Found | Parts Used | Visit Status
📊 VISIT SUMMARY
Total Visits This Month: | [5 empty] | 0
Visits Completed: | [5 empty] | 0
Visits Missed / Overdue: | [5 empty] | 0
Defects Raised: | [5 empty] | 0
Total Hours on Site:
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## AHU PPM
Your HVAC Co. |  |  |  |  | HVAC PPM Checklist
🏭 AIR HANDLING UNIT (AHU) — PLANNED PREVENTIVE MAINTENANCE
Asset ID / Tag: |  |  |  | Visit Date: |  | PPM Ref #:
AHU Location: |  |  |  | Technician Name: |  | Work Order #:
Service Frequency: |  |  |  | Time On / Off: |  | Next PPM Due:
PPM Task Item | Pass | Fail | N/A | Measurement / Reading | Notes / Action
▶ FILTERS
Record filter differential pressure — as found (in. wg) | ☐ | ☐ | ☐
Inspect filter condition: loading, bypass, damage | ☐ | ☐ | ☐
Replace primary filters — record type, MERV, qty | ☐ | ☐ | ☐
Replace secondary / final filters (if applicable) | ☐ | ☐ | ☐
Clean filter housing and rack — remove debris | ☐ | ☐ | ☐
Record filter DP after replacement (in. wg) | ☐ | ☐ | ☐
Record filter media: P/N, MERV rating, qty installed | ☐ | ☐ | ☐
▶ SUPPLY FAN & MOTOR
Inspect fan wheel / blades — clean, balanced, no damage | ☐ | ☐ | ☐
Check fan shaft bearings: noise, vibration, temperature | ☐ | ☐ | ☐
Lubricate fan shaft bearings (non-sealed type) | ☐ | ☐ | ☐
Measure and record motor amps — all 3 phases (A) | ☐ | ☐ | ☐
Measure and record motor voltage — all 3 phases (V) | ☐ | ☐ | ☐
Check motor mounting — tighten bolts if required | ☐ | ☐ | ☐
Check VFD operation, fault log, and speed reference (if fitted) | ☐ | ☐ | ☐
Verify fan rotation direction is correct | ☐ | ☐ | ☐
Record fan RPM (design vs measured) | ☐ | ☐ | ☐
▶ DRIVE BELTS & SHEAVES
Inspect belts — cracking, glazing, fraying, correct tension | ☐ | ☐ | ☐
Measure and adjust belt tension to manufacturer spec | ☐ | ☐ | ☐
Check belt alignment — realign sheaves if required | ☐ | ☐ | ☐
Inspect sheaves — no cracks, worn grooves, or damage | ☐ | ☐ | ☐
Replace belts if worn (record belt size & qty) | ☐ | ☐ | ☐
Record sheave sizes (motor and fan) | ☐ | ☐ | ☐
▶ HEATING & COOLING COILS
Inspect coil fin condition — fouling, damage, frost | ☐ | ☐ | ☐
Clean coil fins if fouling >10% — document method | ☐ | ☐ | ☐
Check coil connections — no refrigerant or water leaks | ☐ | ☐ | ☐
Measure entering air DB temperature (°F) | ☐ | ☐ | ☐
Measure leaving air DB temperature (°F) | ☐ | ☐ | ☐
Measure entering air WB temperature (°F — cooling only) | ☐ | ☐ | ☐
Measure leaving air WB temperature (°F — cooling only) | ☐ | ☐ | ☐
Record coil static pressure drop (in. wg) | ☐ | ☐ | ☐
▶ DRAIN PAN & CONDENSATE
Inspect and clean drain pan — no standing water or algae | ☐ | ☐ | ☐
Flush and test condensate drain — confirm free drainage | ☐ | ☐ | ☐
Prime condensate trap and inspect condition | ☐ | ☐ | ☐
Test condensate pump and float switch (if installed) | ☐ | ☐ | ☐
Check drain pan insulation and vapour barrier integrity | ☐ | ☐ | ☐
▶ DAMPERS, ACTUATORS & CONTROLS
Inspect and operate OSA damper through full range | ☐ | ☐ | ☐
Inspect and operate return air damper and blade seals | ☐ | ☐ | ☐
Test economiser / mixed air damper sequence | ☐ | ☐ | ☐
Calibrate damper actuators — verify position feedback | ☐ | ☐ | ☐
Verify thermostat / controller setpoints — document | ☐ | ☐ | ☐
Test smoke detector and fire/smoke damper (if equipped) | ☐ | ☐ | ☐
Check BAS / DDC points — calibrate if out of tolerance | ☐ | ☐ | ☐
Test unit enable / disable via BMS | ☐ | ☐ | ☐
▶ CABINET, CASING & GENERAL
Inspect unit cabinet — corrosion, loose panels, seal condition | ☐ | ☐ | ☐
Check and replace access door gaskets if deteriorated | ☐ | ☐ | ☐
Clean unit interior — remove dust, debris, foreign objects | ☐ | ☐ | ☐
Inspect flexible duct connections — no tears or splits | ☐ | ☐ | ☐
Check vibration isolators — springs floating, no hard contact | ☐ | ☐ | ☐
Inspect insulation inside AHU casing — no delamination | ☐ | ☐ | ☐
Confirm unit labelling / asset tag is legible | ☐ | ☐ | ☐
Check all access panel fasteners secure | ☐ | ☐ | ☐
✍️ ENGINEER SIGN-OFF
Engineer Name:
Signature & Date:
Supervisor Sign-Off:
Customer Acceptance:
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## RTU PPM
Your HVAC Co. |  |  |  |  | HVAC PPM Checklist
🌬️ ROOFTOP UNIT (RTU) — PLANNED PREVENTIVE MAINTENANCE
Asset ID / Tag: |  |  |  | Visit Date: |  | PPM Ref #:
RTU Location: |  |  |  | Technician Name: |  | Work Order #:
Service Type (Q/SA/A): |  |  |  | Time On / Off: |  | Next PPM Due:
PPM Task Item | Pass | Fail | N/A | Measurement / Reading | Notes / Action
▶ CABINET & UNIT EXTERIOR
Inspect cabinet — corrosion, damage, missing panels | ☐ | ☐ | ☐
Inspect roof curb, flashing, and weather seals | ☐ | ☐ | ☐
Check all access panels — hinges, latches, gaskets | ☐ | ☐ | ☐
Clean unit exterior and clear debris from roof curb | ☐ | ☐ | ☐
Verify unit levelness — check vibration isolators | ☐ | ☐ | ☐
Inspect base frame / structural members — no corrosion | ☐ | ☐ | ☐
▶ FILTERS
Record as-found filter differential pressure (in. wg) | ☐ | ☐ | ☐
Replace filters — record MERV rating, size, qty | ☐ | ☐ | ☐
Verify filter rack seal — no air bypass around frame | ☐ | ☐ | ☐
Record filter DP after replacement (in. wg) | ☐ | ☐ | ☐
▶ SUPPLY FAN
Inspect fan wheel — clean, no damage or imbalance | ☐ | ☐ | ☐
Check bearings — lubricate if non-sealed type | ☐ | ☐ | ☐
Measure motor amps all 3 phases — record vs FLA | ☐ | ☐ | ☐
Measure motor voltage all 3 phases | ☐ | ☐ | ☐
Inspect and adjust belt / sheave drive (if fitted) | ☐ | ☐ | ☐
Check VFD fault log and parameters (if installed) | ☐ | ☐ | ☐
▶ DX COOLING SYSTEM
Record suction pressure (PSIG) | ☐ | ☐ | ☐
Record discharge pressure (PSIG) | ☐ | ☐ | ☐
Calculate and record superheat (°F) — target 8–12°F | ☐ | ☐ | ☐
Calculate and record subcooling (°F) — target 10–15°F | ☐ | ☐ | ☐
Check refrigerant charge — no signs of leak | ☐ | ☐ | ☐
Inspect compressor — noise, vibration, heat | ☐ | ☐ | ☐
Measure compressor amps all 3 phases — record vs FLA | ☐ | ☐ | ☐
Check compressor contactor — contacts, coil, overload | ☐ | ☐ | ☐
Inspect condenser coil — clean fins, no damage | ☐ | ☐ | ☐
Clean condenser coil if fouling present | ☐ | ☐ | ☐
Inspect and test condenser fan(s) — amps, rotation | ☐ | ☐ | ☐
Test high and low pressure safeties | ☐ | ☐ | ☐
Check crankcase heater operation (if equipped) | ☐ | ☐ | ☐
Leak-test refrigerant circuit — record result | ☐ | ☐ | ☐
▶ HEATING SECTION
Inspect heat exchanger / burner — cracks, corrosion | ☐ | ☐ | ☐
Test ignition sequence — spark / glow plug / pilot | ☐ | ☐ | ☐
Inspect flue / vent connection — clear, no gaps | ☐ | ☐ | ☐
Measure supply air temperature in heat mode | ☐ | ☐ | ☐
Test limit switch, rollout switch, and high-temp cutout | ☐ | ☐ | ☐
Check gas valve and manifold for leaks — gas-tight test | ☐ | ☐ | ☐
Check electric heat strips — amp draw vs nameplate | ☐ | ☐ | ☐
▶ CONTROLS & SAFETIES
Verify thermostat / BMS setpoints — document as-found | ☐ | ☐ | ☐
Test economiser controls and damper operation | ☐ | ☐ | ☐
Test smoke detector and fire damper (if equipped) | ☐ | ☐ | ☐
Inspect all wiring — no loose terminals or chafed insulation | ☐ | ☐ | ☐
Check contactors and relays — pitting, overheating | ☐ | ☐ | ☐
Test defrost cycle (heat pump units only) | ☐ | ☐ | ☐
Test fan-proved switch and low-limit controls | ☐ | ☐ | ☐
▶ DRAIN PAN & CONDENSATE
Inspect and clean drain pan | ☐ | ☐ | ☐
Flush condensate drain — confirm free flow | ☐ | ☐ | ☐
Test condensate pump and float switch (if installed) | ☐ | ☐ | ☐
✍️ ENGINEER SIGN-OFF
Engineer Name:
Signature & Date:
Supervisor Sign-Off:
Customer Acceptance:
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Chiller PPM
Your HVAC Co. |  |  |  |  | HVAC PPM Checklist
🧊 CHILLER — PLANNED PREVENTIVE MAINTENANCE
Asset ID / Tag: |  |  |  | Visit Date: |  | PPM Ref #:
Chiller Location: |  |  |  | Technician Name: |  | Work Order #:
Chiller Type (Screw/Scroll/Centrifugal): |  |  |  | Time On / Off: |  | Next PPM Due:
PPM Task Item | Pass | Fail | N/A | Measurement / Reading | Notes / Action
▶ GENERAL INSPECTION
Inspect unit chassis and casing — corrosion, damage, leaks | ☐ | ☐ | ☐
Check oil level / oil pressure (if applicable) | ☐ | ☐ | ☐
Review chiller fault log and operating hours | ☐ | ☐ | ☐
Inspect electrical panel — clean, no rodent damage | ☐ | ☐ | ☐
Verify unit is operating within design parameters | ☐ | ☐ | ☐
▶ REFRIGERATION CIRCUIT
Record suction pressure (PSIG) | ☐ | ☐ | ☐
Record discharge pressure (PSIG) | ☐ | ☐ | ☐
Calculate and record superheat (°F) | ☐ | ☐ | ☐
Calculate and record subcooling (°F) | ☐ | ☐ | ☐
Record leaving chilled water temp (LCWT) °F | ☐ | ☐ | ☐
Record entering chilled water temp (ECWT) °F | ☐ | ☐ | ☐
Record condenser EWT and LWT (water-cooled) °F | ☐ | ☐ | ☐
Leak-test refrigerant circuit — EPA log entry | ☐ | ☐ | ☐
Check refrigerant charge — top up if required, log qty | ☐ | ☐ | ☐
▶ COMPRESSOR
Inspect compressor — vibration, noise, temperature | ☐ | ☐ | ☐
Measure compressor amps all phases — record vs FLA | ☐ | ☐ | ☐
Check compressor oil — level, colour, contamination | ☐ | ☐ | ☐
Inspect compressor mounting and vibration isolators | ☐ | ☐ | ☐
▶ EVAPORATOR & CONDENSER
Inspect evaporator tubes — fouling, scale (water-cooled) | ☐ | ☐ | ☐
Inspect condenser coil fins (air-cooled) — clean if fouled | ☐ | ☐ | ☐
Check condenser tubes (water-cooled) — scaling | ☐ | ☐ | ☐
Measure evaporator approach temperature (°F) | ☐ | ☐ | ☐
Measure condenser approach temperature (°F) | ☐ | ☐ | ☐
▶ PUMPS & PIPEWORK
Inspect chilled water pump — seal, bearings, amps | ☐ | ☐ | ☐
Record chilled water pump DP (ft or PSI) | ☐ | ☐ | ☐
Inspect condenser water pump (if installed) | ☐ | ☐ | ☐
Check expansion vessel pre-charge pressure | ☐ | ☐ | ☐
Inspect all visible pipework — no leaks or corrosion | ☐ | ☐ | ☐
Check strainer baskets — clean if clogged | ☐ | ☐ | ☐
Test glycol concentration (if applicable) — record % | ☐ | ☐ | ☐
▶ CONTROLS & SAFETIES
Verify chilled water setpoint and reset schedule | ☐ | ☐ | ☐
Test high and low pressure safeties | ☐ | ☐ | ☐
Test low flow / freeze protection interlocks | ☐ | ☐ | ☐
Test condenser high-temp cutout (air-cooled) | ☐ | ☐ | ☐
Check BMS integration — trends, alarms, setpoints | ☐ | ☐ | ☐
Calibrate chilled water temp sensors | ☐ | ☐ | ☐
✍️ ENGINEER SIGN-OFF
Engineer Name:
Signature & Date:
Supervisor Sign-Off:
Customer Acceptance:
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Boiler PPM
Your HVAC Co. |  |  |  |  | HVAC PPM Checklist
🔥 BOILER / HEATING PLANT — PLANNED PREVENTIVE MAINTENANCE
Asset ID / Tag: |  |  |  | Visit Date: |  | PPM Ref #:
Boiler Location: |  |  |  | Technician Name: |  | Work Order #:
Boiler Type (Gas/Oil/Electric): |  |  |  | Gas Safe / Reg Cert #: |  | Next PPM Due:
PPM Task Item | Pass | Fail | N/A | Measurement / Reading | Notes / Action
▶ GENERAL INSPECTION
Inspect boiler casing — corrosion, damage, leaks | ☐ | ☐ | ☐
Check system operating pressure (bar / PSI) | ☐ | ☐ | ☐
Record boiler flow and return water temperatures (°F) | ☐ | ☐ | ☐
Check boiler fault log and lockout history | ☐ | ☐ | ☐
Inspect all visible pipework — joints, valves, insulation | ☐ | ☐ | ☐
▶ COMBUSTION & BURNER
Inspect burner head — clean, no distortion or corrosion | ☐ | ☐ | ☐
Clean burner head and flame ports | ☐ | ☐ | ☐
Check and clean ignition electrode — set correct gap | ☐ | ☐ | ☐
Check and clean flame sensor / UV cell | ☐ | ☐ | ☐
Test ignition and flame establishment | ☐ | ☐ | ☐
Carry out flue gas analysis — record CO, CO₂, O₂, efficiency | ☐ | ☐ | ☐
Adjust combustion for optimum efficiency | ☐ | ☐ | ☐
Check gas pressure at test point (mbar / in. wg) | ☐ | ☐ | ☐
Inspect gas train — no leaks, solenoid valves operational | ☐ | ☐ | ☐
Perform gas-tight test on all joints and valves | ☐ | ☐ | ☐
▶ HEAT EXCHANGER & FLUE
Inspect heat exchanger — scaling, corrosion, cracking | ☐ | ☐ | ☐
Clean heat exchanger if required | ☐ | ☐ | ☐
Inspect flue / flue liner — no blockage, damage, or gaps | ☐ | ☐ | ☐
Check flue terminal position — clear of obstructions | ☐ | ☐ | ☐
Inspect condensate drain (condensing boilers) — clear | ☐ | ☐ | ☐
Test CO detector (if installed) — record reading | ☐ | ☐ | ☐
▶ SAFETY DEVICES & CONTROLS
Test high-limit thermostat — operation and setpoint | ☐ | ☐ | ☐
Test pressure relief valve — no weeping, correct setpoint | ☐ | ☐ | ☐
Test low-water cutoff (if applicable) | ☐ | ☐ | ☐
Test over-temperature safety cutout | ☐ | ☐ | ☐
Check and test expansion vessel pressure | ☐ | ☐ | ☐
Verify boiler setpoint and sequence control | ☐ | ☐ | ☐
Test frost protection thermostat (if applicable) | ☐ | ☐ | ☐
Check all safety interlocks — document test results | ☐ | ☐ | ☐
▶ WATER TREATMENT & SYSTEM
Check system inhibitor level — top up if required | ☐ | ☐ | ☐
Record system water pH and hardness | ☐ | ☐ | ☐
Check and clean magnetic filter / strainer | ☐ | ☐ | ☐
Check system pressure and top up if low | ☐ | ☐ | ☐
Inspect all circulating pumps — seal, bearings, amps | ☐ | ☐ | ☐
Test pump duty / standby changeover (if installed) | ☐ | ☐ | ☐
✍️ ENGINEER SIGN-OFF
Engineer Name:
Gas Safe / Reg. Cert #:
Signature & Date:
Customer Acceptance:
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## FCU & Split System PPM
Your HVAC Co. |  |  |  |  | HVAC PPM Checklist
🌡️ FAN COIL UNITS & SPLIT SYSTEMS — PLANNED PREVENTIVE MAINTENANCE
Asset ID / Tag: |  |  |  | Visit Date: |  | PPM Ref #:
Unit Location: |  |  |  | Technician Name: |  | Work Order #:
Unit Type (FCU / Split / Cassette): |  |  |  | Time On / Off: |  | Next PPM Due:
PPM Task Item | Pass | Fail | N/A | Measurement / Reading | Notes / Action
▶ INDOOR / FAN COIL UNIT
Inspect unit casing and grille — no damage or corrosion | ☐ | ☐ | ☐
Remove and clean filter — wash or replace as required | ☐ | ☐ | ☐
Clean evaporator coil fins — no fouling or damage | ☐ | ☐ | ☐
Clean fan blower wheel — no dust accumulation | ☐ | ☐ | ☐
Lubricate fan motor bearings (if non-sealed) | ☐ | ☐ | ☐
Measure fan motor amps | ☐ | ☐ | ☐
Inspect drain pan — clean, no algae or blockage | ☐ | ☐ | ☐
Flush and test condensate drain | ☐ | ☐ | ☐
Check drain pan float switch / condensate pump (if fitted) | ☐ | ☐ | ☐
Verify control valve operation — full open/close cycle | ☐ | ☐ | ☐
Inspect pipe connections at unit — no leaks | ☐ | ☐ | ☐
Measure supply air temperature — cooling mode (°F) | ☐ | ☐ | ☐
Measure supply air temperature — heating mode (°F) | ☐ | ☐ | ☐
Measure return air temperature (°F) | ☐ | ☐ | ☐
▶ OUTDOOR / CONDENSING UNIT
Inspect unit casing — no corrosion, damage, debris | ☐ | ☐ | ☐
Clean condenser coil fins — no fouling (wash if required) | ☐ | ☐ | ☐
Inspect and test condenser fan — blade, bearing, amps | ☐ | ☐ | ☐
Check compressor — noise, vibration, temperature | ☐ | ☐ | ☐
Measure compressor amps all phases | ☐ | ☐ | ☐
Record suction pressure (PSIG) | ☐ | ☐ | ☐
Record discharge pressure (PSIG) | ☐ | ☐ | ☐
Calculate and record superheat (°F) | ☐ | ☐ | ☐
Calculate and record subcooling (°F) | ☐ | ☐ | ☐
Leak-test refrigerant circuit | ☐ | ☐ | ☐
Check refrigerant charge — top up if required, log qty | ☐ | ☐ | ☐
Inspect electrical panel — terminals, contactors, wiring | ☐ | ☐ | ☐
Test capacitors (if accessible) | ☐ | ☐ | ☐
▶ CONTROLS & COMMISSIONING
Test remote controller / wall thermostat operation | ☐ | ☐ | ☐
Verify all operating modes: cool, heat, fan, auto, dry | ☐ | ☐ | ☐
Test timer schedules (if applicable) | ☐ | ☐ | ☐
Check BMS / BACnet integration (if applicable) | ☐ | ☐ | ☐
Test remote enable / disable via BMS | ☐ | ☐ | ☐
Record setpoint, mode, and run hours from controller | ☐ | ☐ | ☐
✍️ ENGINEER SIGN-OFF
Engineer Name:
Signature & Date:
Supervisor Sign-Off:
Customer Acceptance:
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Refrigerant F-Gas Log
Your HVAC Co. | [5 empty] | HVAC PPM Checklist
🧪 REFRIGERANT LOG — F-GAS / EPA 608 COMPLIANCE RECORD
⚠️ Statutory Record: All refrigerant additions, recoveries, and leak checks must be recorded per F-Gas Regulation (EU) No 517/2014 / EPA Section 608. Retain for minimum 5 years.
Date | Asset ID / Tag | Refrigerant Type | System Charge (kg/lbs) | Leaked (kg/lbs) | Added (kg/lbs) | Recovered (kg/lbs) | Net Change | Leak Test Result | Check Frequency Due | Cert / Licence # | Engineer Signature
📊 REFRIGERANT INVENTORY SUMMARY
Total Refrigerant Added (all systems): | [7 empty] | 0
Total Refrigerant Recovered: | [7 empty] | 0
Total Leak Events Recorded: | [7 empty] | 0
Systems Requiring Check — Check Frequency Overdue:
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Deficiency Log
Your HVAC Co. |  |  |  |  | HVAC PPM Checklist
⚠️ DEFICIENCY & REMEDIAL WORKS LOG
# | Date Found | Asset ID | Deficiency Description | Remedial Action Required | Assigned To | Priority | Due Date | Date Closed | PPM Ref # | Status
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
📊 DEFICIENCY SUMMARY
Total Deficiencies Raised: | [5 empty] | 0
Open / In Progress: | [5 empty] | 0
Closed / Resolved: | [5 empty] | 0
Critical Priority: | [5 empty] | 0
High Priority: | [5 empty] | 0
Overdue Items: | [5 empty] | 0
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## KPI & Performance Report
Your HVAC Co. | [5 empty] | HVAC PPM Checklist
📈 PPM KPI & PERFORMANCE REPORT — MONTHLY DASHBOARD
Reporting Period: ¦ Contract: ¦ Site: ¦ Prepared By:
📊 MONTHLY KPI SUMMARY
KPI Metric | Target | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct
PPM Completion Rate (%) | ≥98%
Reactive Call-Outs (count) | ≤5/month
First-Time Fix Rate (%) | ≥85%
Mean Time to Respond (hrs) | ≤4 hrs
Mean Time to Repair (hrs) | ≤8 hrs
System Uptime / Availability (%) | ≥99%
Open Deficiencies — Critical | 0
Open Deficiencies — High | ≤2
Open Deficiencies — Total | ≤10
Customer Satisfaction Score | ≥4.0/5
Refrigerant Leak Events | 0
Energy Performance (index) | Baseline
Planned vs Actual Visits | 100%
Parts Cost vs Budget (%) | ≤100%
📋 VISIT COMPLIANCE TRACKER
Month | Visits Planned | Visits Completed | Visits Missed | Compliance % | YTD Planned | YTD Completed | YTD Compliance %
Jan |  |  |  |  | 0 | 0
Feb |  |  |  |  | 0 | 0
Mar |  |  |  |  | 0 | 0
Apr |  |  |  |  | 0 | 0
May |  |  |  |  | 0 | 0
Jun |  |  |  |  | 0 | 0
Jul |  |  |  |  | 0 | 0
Aug |  |  |  |  | 0 | 0
Sep |  |  |  |  | 0 | 0
Oct |  |  |  |  | 0 | 0
Nov |  |  |  |  | 0 | 0
Dec |  |  |  |  | 0 | 0
ANNUAL TOTALS | 0 | 0 | 0
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Parts & Cost Tracker
Your HVAC Co. |  |  |  |  | HVAC PPM Checklist
💰 PARTS, CONSUMABLES & COST TRACKER
# | Date | Asset ID | Part / Material Description | Part Number | Qty | Unit ($) | Total ($) | Charge Type | WO # | Notes
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
TOTALS | [6 empty] | 0
📊 COST SUMMARY
Total Parts & Materials Cost: |  |  |  |  | 0
PPM Labour Hours (this period):
PPM Labour Rate ($/hr):
Total PPM Labour Cost:
Reactive Callout Costs:
Total Period Cost:
Budget (this period):
Variance vs Budget:
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Summary & Client Sign-Off
Your HVAC Co. | [5 empty] | HVAC PPM Checklist
PLANNED PREVENTIVE MAINTENANCE — PERIOD SUMMARY REPORT
📊 PPM COMPLETION SUMMARY — THIS PERIOD
Equipment Category | Scheduled | Completed | Missed | Comp. % | Defects Found | Open Defects | Category Status
Air Handling Units
Rooftop Units
Fan Coil Units
Split / DX Systems
Chillers
Cooling Towers
Boilers
HVAC Pumps
Exhaust Fans
BMS / Controls
Other
PERIOD TOTALS | 0 | 0 | 0 |  | 0 | 0
📝 OVERALL FINDINGS & NARRATIVE
⚠️ OUTSTANDING ITEMS & RECOMMENDATIONS
✍️ CLIENT ACCEPTANCE & SIGN-OFF
Service Provider Authorised Rep: |  |  | Print Name: |  |  | Signature: |  | Date:
Contract Manager: |  |  | Cert / Reg #: |  |  | Company: |  | Phone:
Client Building Owner / FM: |  |  | Print Name: |  |  | Signature: |  | Date Accepted:
Client Representative: |  |  | Title / Role: |  |  | Comments: |  | Date:
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com