## Cover
Your HVAC Co. | HVAC Quarterly Maintenance Checklist
HVAC QUARTERLY MAINTENANCE CHECKLIST
Scheduled Four-Visit Annual Maintenance Programme
📅 SELECT QUARTER
☐ Q1 — January / February / March ☐ Q2 — April / May / June ☐ Q3 — July / August / September ☐ Q4 — October / November / December
📋 VISIT & SERVICE INFORMATION
Work Order #: | Visit Date:
Quarter / Year: | Next Quarter Due:
Technician Name: | Technician Licence #:
Company / Employer: | Supervisor / Lead Tech:
Customer PO #: | Time On Site (Start / End):
Service Type: | Priority Level:
🏢 SITE & EQUIPMENT INFORMATION
Site / Facility Name: | Site Reference / Code:
Site Address: | City / State / Zip:
Building Type / Use: | Floor / Zone / Area:
Unit / System Tag: | Equipment Type:
Manufacturer: | Model Number:
Serial Number: | Install Year:
Refrigerant Type: | System Capacity:
Drive Type (Belt / Direct / VFD): | Number of Zones:
🌡️ SITE CONDITIONS AT TIME OF VISIT
Outdoor Dry-Bulb Temp (°F): | Outdoor RH (%):
Indoor Dry-Bulb Temp (°F): | Indoor RH (%):
Weather Conditions: | Barometric Pressure (in. Hg):
Unit Operating Mode (Cool/Heat/Fan): | Building Pressurisation Status:
Last Quarterly Visit Date: | Last Filter Change Date:
✅ TECHNICIAN CERTIFICATION & SIGN-OFF
Technician Name: | Signature:
EPA 608 / Cert #: | Date Completed:
Reviewed / Approved By: | Customer Acceptance:
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Quarterly Task Matrix
Your HVAC Co. | [6 empty] | HVAC Quarterly Maintenance Checklist
📋 QUARTERLY MAINTENANCE TASK MATRIX — FULL YEAR OVERVIEW
LEGEND: ✓ = Completed ✗ = Failed / Defect Found — = N/A ○ = Scheduled / Pending ● = In Progress
Maintenance Task | Q1 Status | Q2 Status | Q3 Status | Q4 Status | Frequency | Responsible | Jan | Feb | Mar | Apr | May | Jun | Jul
▶ FILTERS & AIR QUALITY
Inspect & replace primary air filters | ○ | ○ | ○ | ○ | Q | Technician
Record filter differential pressure (as-found & as-left) | ○ | ○ | ○ | ○ | Q | Technician
Clean filter housing and rack | ○ | ○ | ○ | ○ | Q | Technician
Inspect secondary / HEPA filters (if applicable) | ○ | ○ | ○ | ○ | Q | Technician
Check & calibrate IAQ / CO₂ sensors | ○ | ○ | ○ | ○ | SA | Controls Tech
Replace carbon / activated charcoal filters (if fitted) | ○ | ○ | ○ | ○ | SA | Technician
▶ FAN & MOTOR
Inspect fan wheel / blades — clean and balance check | ○ | ○ | ○ | ○ | Q | Technician
Lubricate fan shaft bearings (non-sealed) | ○ | ○ | ○ | ○ | Q | Technician
Check fan belt condition, tension, and alignment | ○ | ○ | ○ | ○ | Q | Technician
Measure motor amps — all phases (compare to FLA) | ○ | ○ | ○ | ○ | Q | Technician
Measure motor voltage — all phases (check imbalance) | ○ | ○ | ○ | ○ | Q | Technician
Check VFD operation and fault log (if installed) | ○ | ○ | ○ | ○ | Q | Controls Tech
Megger motor winding insulation resistance | ○ | ○ | ○ | ○ | A | Technician
Inspect sheave condition and alignment | ○ | ○ | ○ | ○ | SA | Technician
▶ COILS & HEAT EXCHANGE
Inspect evaporator coil — fouling, frost, damage | ○ | ○ | ○ | ○ | Q | Technician
Clean evaporator coil fins (chemical wash if required) | ○ | ○ | ○ | ○ | SA | Technician
Inspect condenser coil — fouling, damage | ○ | ○ | ○ | ○ | Q | Technician
Clean condenser coil (pressure wash if required) | ○ | ○ | ○ | ○ | SA | Technician
Measure coil entering/leaving air temperature (DB & WB) | ○ | ○ | ○ | ○ | Q | Technician
Check coil connections — refrigerant or hydronic leaks | ○ | ○ | ○ | ○ | Q | Technician
Record coil static pressure drop | ○ | ○ | ○ | ○ | Q | Technician
▶ REFRIGERATION / DX SYSTEM
Record suction & discharge pressures | ○ | ○ | ○ | ○ | Q | Technician
Calculate & record superheat and subcooling | ○ | ○ | ○ | ○ | Q | Technician
Full refrigerant leak check — F-Gas / EPA log entry | ○ | ○ | ○ | ○ | Q | Technician
Check compressor operation — noise, vibration, heat | ○ | ○ | ○ | ○ | Q | Technician
Measure compressor amps — all phases | ○ | ○ | ○ | ○ | Q | Technician
Test high & low pressure safety controls | ○ | ○ | ○ | ○ | SA | Technician
Check crankcase heater operation (if equipped) | ○ | ○ | ○ | ○ | Q | Technician
Test TXV / EXV operation (if accessible) | ○ | ○ | ○ | ○ | A | Refrigeration Tech
▶ DRAIN PAN & CONDENSATE
Inspect & clean drain pan — no algae or standing water | ○ | ○ | ○ | ○ | Q | Technician
Flush & test condensate drain line | ○ | ○ | ○ | ○ | Q | Technician
Prime condensate trap | ○ | ○ | ○ | ○ | Q | Technician
Test condensate pump and float switch (if installed) | ○ | ○ | ○ | ○ | Q | Technician
Inspect drain pan insulation integrity | ○ | ○ | ○ | ○ | SA | Technician
▶ ELECTRICAL & CONTROLS
Check & tighten all electrical terminal connections | ○ | ○ | ○ | ○ | SA | Electrician
Inspect contactors — contacts, coil, overload settings | ○ | ○ | ○ | ○ | Q | Technician
Test capacitors (if accessible) | ○ | ○ | ○ | ○ | SA | Technician
Verify all safety & control setpoints — document | ○ | ○ | ○ | ○ | Q | Controls Tech
Test smoke detector / fire damper (if equipped) | ○ | ○ | ○ | ○ | A | Controls Tech
Calibrate thermostat / BAS sensors | ○ | ○ | ○ | ○ | SA | Controls Tech
Check BAS / DDC integration and alarm history | ○ | ○ | ○ | ○ | Q | Controls Tech
Verify economiser operation (if applicable) | ○ | ○ | ○ | ○ | Q | Controls Tech
▶ DUCTWORK & AIRSIDE
Inspect accessible ductwork — no leaks or damage | ○ | ○ | ○ | ○ | SA | Technician
Check & operate balancing dampers | ○ | ○ | ○ | ○ | Q | Technician
Inspect flexible duct connections — no tears or splits | ○ | ○ | ○ | ○ | Q | Technician
Measure & record supply air CFM (key terminals) | ○ | ○ | ○ | ○ | SA | Technician
Inspect VAV boxes / terminal units (if installed) | ○ | ○ | ○ | ○ | Q | Controls Tech
▶ HYDRONIC SYSTEM (IF APPLICABLE)
Check system pressure and top up if required | ○ | ○ | ○ | ○ | Q | Technician
Test glycol / inhibitor concentration | ○ | ○ | ○ | ○ | Q | Technician
Inspect pump seals, bearings, and amp draw | ○ | ○ | ○ | ○ | Q | Technician
Clean strainer baskets | ○ | ○ | ○ | ○ | Q | Technician
Check expansion vessel pre-charge pressure | ○ | ○ | ○ | ○ | SA | Technician
Test chemical treatment levels | ○ | ○ | ○ | ○ | Q | Technician
▶ GENERAL & SAFETY
Inspect unit cabinet — corrosion, loose panels, seals | ○ | ○ | ○ | ○ | Q | Technician
Check vibration isolators — springs floating | ○ | ○ | ○ | ○ | Q | Technician
Clean unit interior — remove dust and debris | ○ | ○ | ○ | ○ | Q | Technician
Confirm unit labelling / asset tag is legible | ○ | ○ | ○ | ○ | Q | Technician
Review fault log / alarm history — document findings | ○ | ○ | ○ | ○ | Q | Technician
Complete deficiency log for all failed items | ○ | ○ | ○ | ○ | Q | Technician
📊 ANNUAL COMPLETION SUMMARY
Total Tasks on Matrix: |  |  |  |  | 68
Q1 — Tasks Completed: |  |  |  |  | 0
Q2 — Tasks Completed: |  |  |  |  | 0
Q3 — Tasks Completed: |  |  |  |  | 0
Q4 — Tasks Completed: |  |  |  |  | 0
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Q1 Checklist (Jan–Mar)
Your HVAC Co. |  |  |  |  | HVAC Quarterly Maintenance Checklist
🗓️ Q1 — JANUARY / FEBRUARY / MARCH — QUARTERLY MAINTENANCE CHECKLIST
Asset ID / Tag: |  |  |  | Visit Date: |  | PPM / WO Ref #:
Unit Location: |  |  |  | Technician Name: |  | Quarter / Year:
Service Type: |  |  |  | Time On / Off: |  | Next Quarter Due:
Task / Inspection Item | Pass | Fail | N/A | Measurement / Reading | Notes / Corrective Action
▶ FILTERS
Record as-found filter differential pressure (in. wg) | ☐ | ☐ | ☐
Inspect filter condition — loading, bypass, damage | ☐ | ☐ | ☐
Replace primary filters — record MERV, size, qty | ☐ | ☐ | ☐
Replace secondary filters if required | ☐ | ☐ | ☐
Clean filter housing and rack | ☐ | ☐ | ☐
Record as-left filter differential pressure (in. wg) | ☐ | ☐ | ☐
Document filter P/N, MERV rating, quantity installed | ☐ | ☐ | ☐
▶ SUPPLY FAN & MOTOR
Inspect fan wheel / blades — clean, no damage or imbalance | ☐ | ☐ | ☐
Check fan shaft bearings — noise, vibration, heat | ☐ | ☐ | ☐
Lubricate fan bearings (non-sealed type only) | ☐ | ☐ | ☐
Measure & record motor amps — L1 / L2 / L3 (A) | ☐ | ☐ | ☐
Measure & record motor voltage — L1-L2 / L2-L3 / L1-L3 (V) | ☐ | ☐ | ☐
Check VFD operation and review fault log (if installed) | ☐ | ☐ | ☐
Check motor mount — tighten bolts if required | ☐ | ☐ | ☐
Verify fan rotation direction | ☐ | ☐ | ☐
▶ DRIVE BELTS & SHEAVES
Inspect belts — cracking, glazing, fraying, correct tension | ☐ | ☐ | ☐
Measure & adjust belt tension to manufacturer spec | ☐ | ☐ | ☐
Check belt alignment — realign sheaves if required | ☐ | ☐ | ☐
Inspect sheave condition — no cracks, worn grooves | ☐ | ☐ | ☐
Replace belts if condemned — record belt size & qty | ☐ | ☐ | ☐
▶ COILS & HEAT EXCHANGE
Inspect evaporator / cooling coil — fouling, frost, fin damage | ☐ | ☐ | ☐
Inspect heating coil — no damage, scale, fouling | ☐ | ☐ | ☐
Check coil connections — no refrigerant or water leaks | ☐ | ☐ | ☐
Measure & record entering air dry-bulb temperature (°F) | ☐ | ☐ | ☐
Measure & record leaving air dry-bulb temperature (°F) | ☐ | ☐ | ☐
Measure & record entering air wet-bulb temp (°F — cooling) | ☐ | ☐ | ☐
Measure & record leaving air wet-bulb temp (°F — cooling) | ☐ | ☐ | ☐
▶ DX / REFRIGERATION SYSTEM
Record suction line pressure (PSIG) | ☐ | ☐ | ☐
Record discharge line pressure (PSIG) | ☐ | ☐ | ☐
Calculate & record superheat (°F) — target 8–12°F | ☐ | ☐ | ☐
Calculate & record subcooling (°F) — target 10–15°F | ☐ | ☐ | ☐
Check refrigerant charge — no signs of leak | ☐ | ☐ | ☐
Inspect compressor — noise, vibration, temperature | ☐ | ☐ | ☐
Measure compressor amps — all phases | ☐ | ☐ | ☐
Check compressor contactor — contacts, coil, overload | ☐ | ☐ | ☐
Leak-test refrigerant circuit — log per F-Gas / EPA 608 | ☐ | ☐ | ☐
▶ DRAIN PAN & CONDENSATE
Inspect & clean drain pan — no algae or standing water | ☐ | ☐ | ☐
Flush & test condensate drain line | ☐ | ☐ | ☐
Prime condensate trap | ☐ | ☐ | ☐
Test condensate pump & float switch (if installed) | ☐ | ☐ | ☐
▶ DAMPERS & CONTROLS
Inspect OSA damper — clean, full range of motion | ☐ | ☐ | ☐
Inspect return air damper — blade seals and linkage | ☐ | ☐ | ☐
Verify thermostat / controller setpoints — document | ☐ | ☐ | ☐
Check BAS / DDC points — calibrate if out of tolerance | ☐ | ☐ | ☐
Test economiser damper sequence (if applicable) | ☐ | ☐ | ☐
Check contactors and relays — pitting, overheating | ☐ | ☐ | ☐
Verify all operating modes — cool, heat, fan, auto | ☐ | ☐ | ☐
▶ CABINET & GENERAL
Inspect unit cabinet — corrosion, loose panels, seal condition | ☐ | ☐ | ☐
Clean unit interior — remove dust, debris, foreign objects | ☐ | ☐ | ☐
Check vibration isolators — springs floating, no hard contact | ☐ | ☐ | ☐
Inspect flexible connections — no tears or splits | ☐ | ☐ | ☐
Check all access panel fasteners secure | ☐ | ☐ | ☐
Confirm asset label / equipment tag is legible | ☐ | ☐ | ☐
Review unit fault / alarm log — document findings | ☐ | ☐ | ☐
📊 Q1 — JANUARY / FEBRUARY / MARCH SUMMARY
Items Inspected:
Items Passed:
Items Failed:
Deficiencies Raised:
✍️ ENGINEER SIGN-OFF
Engineer Name:
Signature & Date:
Supervisor Sign-Off:
Customer Acceptance / Signature:
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Q2 Checklist (Apr–Jun)
Your HVAC Co. |  |  |  |  | HVAC Quarterly Maintenance Checklist
🗓️ Q2 — APRIL / MAY / JUNE — QUARTERLY MAINTENANCE CHECKLIST
Asset ID / Tag: |  |  |  | Visit Date: |  | PPM / WO Ref #:
Unit Location: |  |  |  | Technician Name: |  | Quarter / Year:
Service Type: |  |  |  | Time On / Off: |  | Next Quarter Due:
Task / Inspection Item | Pass | Fail | N/A | Measurement / Reading | Notes / Corrective Action
▶ FILTERS
Record as-found filter differential pressure (in. wg) | ☐ | ☐ | ☐
Inspect filter condition — loading, bypass, damage | ☐ | ☐ | ☐
Replace primary filters — record MERV, size, qty | ☐ | ☐ | ☐
Replace secondary filters if required | ☐ | ☐ | ☐
Clean filter housing and rack | ☐ | ☐ | ☐
Record as-left filter differential pressure (in. wg) | ☐ | ☐ | ☐
Document filter P/N, MERV rating, quantity installed | ☐ | ☐ | ☐
▶ SUPPLY FAN & MOTOR
Inspect fan wheel / blades — clean, no damage or imbalance | ☐ | ☐ | ☐
Check fan shaft bearings — noise, vibration, heat | ☐ | ☐ | ☐
Lubricate fan bearings (non-sealed type only) | ☐ | ☐ | ☐
Measure & record motor amps — L1 / L2 / L3 (A) | ☐ | ☐ | ☐
Measure & record motor voltage — L1-L2 / L2-L3 / L1-L3 (V) | ☐ | ☐ | ☐
Check VFD operation and review fault log (if installed) | ☐ | ☐ | ☐
Check motor mount — tighten bolts if required | ☐ | ☐ | ☐
Verify fan rotation direction | ☐ | ☐ | ☐
▶ DRIVE BELTS & SHEAVES
Inspect belts — cracking, glazing, fraying, correct tension | ☐ | ☐ | ☐
Measure & adjust belt tension to manufacturer spec | ☐ | ☐ | ☐
Check belt alignment — realign sheaves if required | ☐ | ☐ | ☐
Inspect sheave condition — no cracks, worn grooves | ☐ | ☐ | ☐
Replace belts if condemned — record belt size & qty | ☐ | ☐ | ☐
▶ COILS & HEAT EXCHANGE
Inspect evaporator / cooling coil — fouling, frost, fin damage | ☐ | ☐ | ☐
Inspect heating coil — no damage, scale, fouling | ☐ | ☐ | ☐
Check coil connections — no refrigerant or water leaks | ☐ | ☐ | ☐
Measure & record entering air dry-bulb temperature (°F) | ☐ | ☐ | ☐
Measure & record leaving air dry-bulb temperature (°F) | ☐ | ☐ | ☐
Measure & record entering air wet-bulb temp (°F — cooling) | ☐ | ☐ | ☐
Measure & record leaving air wet-bulb temp (°F — cooling) | ☐ | ☐ | ☐
▶ DX / REFRIGERATION SYSTEM
Record suction line pressure (PSIG) | ☐ | ☐ | ☐
Record discharge line pressure (PSIG) | ☐ | ☐ | ☐
Calculate & record superheat (°F) — target 8–12°F | ☐ | ☐ | ☐
Calculate & record subcooling (°F) — target 10–15°F | ☐ | ☐ | ☐
Check refrigerant charge — no signs of leak | ☐ | ☐ | ☐
Inspect compressor — noise, vibration, temperature | ☐ | ☐ | ☐
Measure compressor amps — all phases | ☐ | ☐ | ☐
Check compressor contactor — contacts, coil, overload | ☐ | ☐ | ☐
Leak-test refrigerant circuit — log per F-Gas / EPA 608 | ☐ | ☐ | ☐
▶ DRAIN PAN & CONDENSATE
Inspect & clean drain pan — no algae or standing water | ☐ | ☐ | ☐
Flush & test condensate drain line | ☐ | ☐ | ☐
Prime condensate trap | ☐ | ☐ | ☐
Test condensate pump & float switch (if installed) | ☐ | ☐ | ☐
▶ DAMPERS & CONTROLS
Inspect OSA damper — clean, full range of motion | ☐ | ☐ | ☐
Inspect return air damper — blade seals and linkage | ☐ | ☐ | ☐
Verify thermostat / controller setpoints — document | ☐ | ☐ | ☐
Check BAS / DDC points — calibrate if out of tolerance | ☐ | ☐ | ☐
Test economiser damper sequence (if applicable) | ☐ | ☐ | ☐
Check contactors and relays — pitting, overheating | ☐ | ☐ | ☐
Verify all operating modes — cool, heat, fan, auto | ☐ | ☐ | ☐
▶ CABINET & GENERAL
Inspect unit cabinet — corrosion, loose panels, seal condition | ☐ | ☐ | ☐
Clean unit interior — remove dust, debris, foreign objects | ☐ | ☐ | ☐
Check vibration isolators — springs floating, no hard contact | ☐ | ☐ | ☐
Inspect flexible connections — no tears or splits | ☐ | ☐ | ☐
Check all access panel fasteners secure | ☐ | ☐ | ☐
Confirm asset label / equipment tag is legible | ☐ | ☐ | ☐
Review unit fault / alarm log — document findings | ☐ | ☐ | ☐
📊 Q2 — APRIL / MAY / JUNE SUMMARY
Items Inspected:
Items Passed:
Items Failed:
Deficiencies Raised:
✍️ ENGINEER SIGN-OFF
Engineer Name:
Signature & Date:
Supervisor Sign-Off:
Customer Acceptance / Signature:
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Q3 Checklist (Jul–Sep)
Your HVAC Co. |  |  |  |  | HVAC Quarterly Maintenance Checklist
🗓️ Q3 — JULY / AUGUST / SEPTEMBER — QUARTERLY MAINTENANCE CHECKLIST
Asset ID / Tag: |  |  |  | Visit Date: |  | PPM / WO Ref #:
Unit Location: |  |  |  | Technician Name: |  | Quarter / Year:
Service Type: |  |  |  | Time On / Off: |  | Next Quarter Due:
Task / Inspection Item | Pass | Fail | N/A | Measurement / Reading | Notes / Corrective Action
▶ FILTERS
Record as-found filter differential pressure (in. wg) | ☐ | ☐ | ☐
Inspect filter condition — loading, bypass, damage | ☐ | ☐ | ☐
Replace primary filters — record MERV, size, qty | ☐ | ☐ | ☐
Replace secondary filters if required | ☐ | ☐ | ☐
Clean filter housing and rack | ☐ | ☐ | ☐
Record as-left filter differential pressure (in. wg) | ☐ | ☐ | ☐
Document filter P/N, MERV rating, quantity installed | ☐ | ☐ | ☐
▶ SUPPLY FAN & MOTOR
Inspect fan wheel / blades — clean, no damage or imbalance | ☐ | ☐ | ☐
Check fan shaft bearings — noise, vibration, heat | ☐ | ☐ | ☐
Lubricate fan bearings (non-sealed type only) | ☐ | ☐ | ☐
Measure & record motor amps — L1 / L2 / L3 (A) | ☐ | ☐ | ☐
Measure & record motor voltage — L1-L2 / L2-L3 / L1-L3 (V) | ☐ | ☐ | ☐
Check VFD operation and review fault log (if installed) | ☐ | ☐ | ☐
Check motor mount — tighten bolts if required | ☐ | ☐ | ☐
Verify fan rotation direction | ☐ | ☐ | ☐
▶ DRIVE BELTS & SHEAVES
Inspect belts — cracking, glazing, fraying, correct tension | ☐ | ☐ | ☐
Measure & adjust belt tension to manufacturer spec | ☐ | ☐ | ☐
Check belt alignment — realign sheaves if required | ☐ | ☐ | ☐
Inspect sheave condition — no cracks, worn grooves | ☐ | ☐ | ☐
Replace belts if condemned — record belt size & qty | ☐ | ☐ | ☐
▶ COILS & HEAT EXCHANGE
Inspect evaporator / cooling coil — fouling, frost, fin damage | ☐ | ☐ | ☐
Inspect heating coil — no damage, scale, fouling | ☐ | ☐ | ☐
Check coil connections — no refrigerant or water leaks | ☐ | ☐ | ☐
Measure & record entering air dry-bulb temperature (°F) | ☐ | ☐ | ☐
Measure & record leaving air dry-bulb temperature (°F) | ☐ | ☐ | ☐
Measure & record entering air wet-bulb temp (°F — cooling) | ☐ | ☐ | ☐
Measure & record leaving air wet-bulb temp (°F — cooling) | ☐ | ☐ | ☐
▶ DX / REFRIGERATION SYSTEM
Record suction line pressure (PSIG) | ☐ | ☐ | ☐
Record discharge line pressure (PSIG) | ☐ | ☐ | ☐
Calculate & record superheat (°F) — target 8–12°F | ☐ | ☐ | ☐
Calculate & record subcooling (°F) — target 10–15°F | ☐ | ☐ | ☐
Check refrigerant charge — no signs of leak | ☐ | ☐ | ☐
Inspect compressor — noise, vibration, temperature | ☐ | ☐ | ☐
Measure compressor amps — all phases | ☐ | ☐ | ☐
Check compressor contactor — contacts, coil, overload | ☐ | ☐ | ☐
Leak-test refrigerant circuit — log per F-Gas / EPA 608 | ☐ | ☐ | ☐
▶ DRAIN PAN & CONDENSATE
Inspect & clean drain pan — no algae or standing water | ☐ | ☐ | ☐
Flush & test condensate drain line | ☐ | ☐ | ☐
Prime condensate trap | ☐ | ☐ | ☐
Test condensate pump & float switch (if installed) | ☐ | ☐ | ☐
▶ DAMPERS & CONTROLS
Inspect OSA damper — clean, full range of motion | ☐ | ☐ | ☐
Inspect return air damper — blade seals and linkage | ☐ | ☐ | ☐
Verify thermostat / controller setpoints — document | ☐ | ☐ | ☐
Check BAS / DDC points — calibrate if out of tolerance | ☐ | ☐ | ☐
Test economiser damper sequence (if applicable) | ☐ | ☐ | ☐
Check contactors and relays — pitting, overheating | ☐ | ☐ | ☐
Verify all operating modes — cool, heat, fan, auto | ☐ | ☐ | ☐
▶ CABINET & GENERAL
Inspect unit cabinet — corrosion, loose panels, seal condition | ☐ | ☐ | ☐
Clean unit interior — remove dust, debris, foreign objects | ☐ | ☐ | ☐
Check vibration isolators — springs floating, no hard contact | ☐ | ☐ | ☐
Inspect flexible connections — no tears or splits | ☐ | ☐ | ☐
Check all access panel fasteners secure | ☐ | ☐ | ☐
Confirm asset label / equipment tag is legible | ☐ | ☐ | ☐
Review unit fault / alarm log — document findings | ☐ | ☐ | ☐
📊 Q3 — JULY / AUGUST / SEPTEMBER SUMMARY
Items Inspected:
Items Passed:
Items Failed:
Deficiencies Raised:
✍️ ENGINEER SIGN-OFF
Engineer Name:
Signature & Date:
Supervisor Sign-Off:
Customer Acceptance / Signature:
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Q4 Checklist (Oct–Dec)
Your HVAC Co. |  |  |  |  | HVAC Quarterly Maintenance Checklist
🗓️ Q4 — OCTOBER / NOVEMBER / DECEMBER — QUARTERLY MAINTENANCE CHECKLIST
Asset ID / Tag: |  |  |  | Visit Date: |  | PPM / WO Ref #:
Unit Location: |  |  |  | Technician Name: |  | Quarter / Year:
Service Type: |  |  |  | Time On / Off: |  | Next Quarter Due:
Task / Inspection Item | Pass | Fail | N/A | Measurement / Reading | Notes / Corrective Action
▶ FILTERS
Record as-found filter differential pressure (in. wg) | ☐ | ☐ | ☐
Inspect filter condition — loading, bypass, damage | ☐ | ☐ | ☐
Replace primary filters — record MERV, size, qty | ☐ | ☐ | ☐
Replace secondary filters if required | ☐ | ☐ | ☐
Clean filter housing and rack | ☐ | ☐ | ☐
Record as-left filter differential pressure (in. wg) | ☐ | ☐ | ☐
Document filter P/N, MERV rating, quantity installed | ☐ | ☐ | ☐
▶ SUPPLY FAN & MOTOR
Inspect fan wheel / blades — clean, no damage or imbalance | ☐ | ☐ | ☐
Check fan shaft bearings — noise, vibration, heat | ☐ | ☐ | ☐
Lubricate fan bearings (non-sealed type only) | ☐ | ☐ | ☐
Measure & record motor amps — L1 / L2 / L3 (A) | ☐ | ☐ | ☐
Measure & record motor voltage — L1-L2 / L2-L3 / L1-L3 (V) | ☐ | ☐ | ☐
Check VFD operation and review fault log (if installed) | ☐ | ☐ | ☐
Check motor mount — tighten bolts if required | ☐ | ☐ | ☐
Verify fan rotation direction | ☐ | ☐ | ☐
▶ DRIVE BELTS & SHEAVES
Inspect belts — cracking, glazing, fraying, correct tension | ☐ | ☐ | ☐
Measure & adjust belt tension to manufacturer spec | ☐ | ☐ | ☐
Check belt alignment — realign sheaves if required | ☐ | ☐ | ☐
Inspect sheave condition — no cracks, worn grooves | ☐ | ☐ | ☐
Replace belts if condemned — record belt size & qty | ☐ | ☐ | ☐
▶ COILS & HEAT EXCHANGE
Inspect evaporator / cooling coil — fouling, frost, fin damage | ☐ | ☐ | ☐
Inspect heating coil — no damage, scale, fouling | ☐ | ☐ | ☐
Check coil connections — no refrigerant or water leaks | ☐ | ☐ | ☐
Measure & record entering air dry-bulb temperature (°F) | ☐ | ☐ | ☐
Measure & record leaving air dry-bulb temperature (°F) | ☐ | ☐ | ☐
Measure & record entering air wet-bulb temp (°F — cooling) | ☐ | ☐ | ☐
Measure & record leaving air wet-bulb temp (°F — cooling) | ☐ | ☐ | ☐
▶ DX / REFRIGERATION SYSTEM
Record suction line pressure (PSIG) | ☐ | ☐ | ☐
Record discharge line pressure (PSIG) | ☐ | ☐ | ☐
Calculate & record superheat (°F) — target 8–12°F | ☐ | ☐ | ☐
Calculate & record subcooling (°F) — target 10–15°F | ☐ | ☐ | ☐
Check refrigerant charge — no signs of leak | ☐ | ☐ | ☐
Inspect compressor — noise, vibration, temperature | ☐ | ☐ | ☐
Measure compressor amps — all phases | ☐ | ☐ | ☐
Check compressor contactor — contacts, coil, overload | ☐ | ☐ | ☐
Leak-test refrigerant circuit — log per F-Gas / EPA 608 | ☐ | ☐ | ☐
▶ DRAIN PAN & CONDENSATE
Inspect & clean drain pan — no algae or standing water | ☐ | ☐ | ☐
Flush & test condensate drain line | ☐ | ☐ | ☐
Prime condensate trap | ☐ | ☐ | ☐
Test condensate pump & float switch (if installed) | ☐ | ☐ | ☐
▶ DAMPERS & CONTROLS
Inspect OSA damper — clean, full range of motion | ☐ | ☐ | ☐
Inspect return air damper — blade seals and linkage | ☐ | ☐ | ☐
Verify thermostat / controller setpoints — document | ☐ | ☐ | ☐
Check BAS / DDC points — calibrate if out of tolerance | ☐ | ☐ | ☐
Test economiser damper sequence (if applicable) | ☐ | ☐ | ☐
Check contactors and relays — pitting, overheating | ☐ | ☐ | ☐
Verify all operating modes — cool, heat, fan, auto | ☐ | ☐ | ☐
▶ CABINET & GENERAL
Inspect unit cabinet — corrosion, loose panels, seal condition | ☐ | ☐ | ☐
Clean unit interior — remove dust, debris, foreign objects | ☐ | ☐ | ☐
Check vibration isolators — springs floating, no hard contact | ☐ | ☐ | ☐
Inspect flexible connections — no tears or splits | ☐ | ☐ | ☐
Check all access panel fasteners secure | ☐ | ☐ | ☐
Confirm asset label / equipment tag is legible | ☐ | ☐ | ☐
Review unit fault / alarm log — document findings | ☐ | ☐ | ☐
📊 Q4 — OCTOBER / NOVEMBER / DECEMBER SUMMARY
Items Inspected:
Items Passed:
Items Failed:
Deficiencies Raised:
✍️ ENGINEER SIGN-OFF
Engineer Name:
Signature & Date:
Supervisor Sign-Off:
Customer Acceptance / Signature:
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Refrigeration Data Log
Your HVAC Co. |  |  |  |  | HVAC Quarterly Maintenance Checklist
❄️ REFRIGERATION & DX SYSTEM — QUARTERLY DATA LOG
Parameter | Q1 Reading | Q1 Status | Q2 Reading | Q2 Status | Q3 Reading | Q3 Status | Q4 Reading | Q4 Status | Unit / Spec
Refrigerant Type | [8 empty] | — / —
Outdoor Ambient Temp (°F) | [8 empty] | °F / —
Suction Pressure | [8 empty] | PSIG / Per Mfr
Discharge Pressure | [8 empty] | PSIG / Per Mfr
Suction Saturation Temp | [8 empty] | °F / Per Mfr
Discharge Saturation Temp | [8 empty] | °F / Per Mfr
Suction Line Temperature | [8 empty] | °F / Per Mfr
Superheat (Suction) | [8 empty] | °F / 8–12°F
Liquid Line Temperature | [8 empty] | °F / Per Mfr
Subcooling (Liquid) | [8 empty] | °F / 10–15°F
Compressor Discharge Temp | [8 empty] | °F / <225°F
Evaporator EAT — Dry Bulb | [8 empty] | °F / —
Evaporator LAT — Dry Bulb | [8 empty] | °F / —
Evaporator EAT — Wet Bulb | [8 empty] | °F / —
Evaporator LAT — Wet Bulb | [8 empty] | °F / —
Evaporator Delta-T (DB) | [8 empty] | °F / 15–20°F
Compressor Amps — L1 | [8 empty] | Amps / <FLA
Compressor Amps — L2 | [8 empty] | Amps / <FLA
Compressor Amps — L3 | [8 empty] | Amps / <FLA
Condenser Fan Amps | [8 empty] | Amps / <FLA
Supply Fan Amps — L1 | [8 empty] | Amps / <FLA
Voltage L1–L2 | [8 empty] | Volts / ±5%
Voltage L2–L3 | [8 empty] | Volts / ±5%
Voltage Imbalance (%) | [8 empty] | <2% / <2%
🧪 REFRIGERANT CHARGE LOG
Quarter | Date | Refrigerant Added (lbs) | Refrigerant Recovered (lbs) | Net Change | Reason | EPA / Cert # | Technician
Q1 (Jan–Mar)
Q2 (Apr–Jun)
Q3 (Jul–Sep)
Q4 (Oct–Dec)
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Electrical & Motor Data
Your HVAC Co. |  |  |  |  | HVAC Quarterly Maintenance Checklist
⚡ ELECTRICAL & MOTOR DATA — QUARTERLY LOG
Parameter | Q1 Reading | Q1 Status | Q2 Reading | Q2 Status | Q3 Reading | Q3 Status | Q4 Reading | Q4 Status | Unit / Spec
Supply Voltage L1–L2 | [8 empty] | Volts / ±5%
Supply Voltage L2–L3 | [8 empty] | Volts / ±5%
Supply Voltage L1–L3 | [8 empty] | Volts / ±5%
Voltage Imbalance (%) | [8 empty] | <2% / <2%
Supply Fan Motor FLA (Nameplate) | [8 empty] | Amps / —
Supply Fan Amps — L1 | [8 empty] | Amps / <FLA
Supply Fan Amps — L2 | [8 empty] | Amps / <FLA
Supply Fan Amps — L3 | [8 empty] | Amps / <FLA
Condenser Fan FLA (Nameplate) | [8 empty] | Amps / —
Condenser Fan Amps | [8 empty] | Amps / <FLA
Compressor FLA (Nameplate) | [8 empty] | Amps / —
Compressor Amps — L1 | [8 empty] | Amps / <FLA
Compressor Amps — L2 | [8 empty] | Amps / <FLA
Compressor Amps — L3 | [8 empty] | Amps / <FLA
Control Circuit Voltage | [8 empty] | Volts / ±10%
Fan RPM (Design vs Measured) | [8 empty] | RPM / ±5%
Filter DP — As Found | [8 empty] | in. wg / —
Filter DP — As Left | [8 empty] | in. wg / —
🎛️ CONTROLS & SETPOINT VERIFICATION — QUARTERLY
Control Parameter | Q1 As-Found | Q1 As-Left | Q2 As-Found | Q2 As-Left | Q3 As-Found | Q3 As-Left | Q4 As-Found | Q4 As-Left | Design Setpoint
Cooling Setpoint (°F)
Heating Setpoint (°F)
Deadband / Differential (°F)
Supply Air Setpoint (°F)
OSA Minimum Position (%)
High Pressure Cutout (PSIG)
Low Pressure Cutout (PSIG)
Freeze Stat Setpoint (°F)
Fan Proven Switch — Test Result
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Air Balance & Airflow Log
Your HVAC Co. | [5 empty] | HVAC Quarterly Maintenance Checklist
💨 AIR BALANCE & AIRFLOW — QUARTERLY MEASUREMENT LOG
Terminal / Duct ID | Location / Zone | Design CFM | Q1 Measured | Q2 Measured | Q3 Measured | Q4 Measured | Q1 % Design | Q2 % Design | Q3 % Design | Q4 % Design | Notes
SYSTEM TOTALS |  | 0 | 0 | 0 | 0 | 0
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Parts & Materials Log
Your HVAC Co. |  |  |  |  | HVAC Quarterly Maintenance Checklist
🔩 PARTS, MATERIALS & CONSUMABLES LOG
# | Qtr | Part / Material Name | Part Number / Description | Manufacturer | Qty | Unit | Unit Cost ($) | Total ($) | Warranty? | Notes
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
TOTALS | [7 empty] | 0
💰 QUARTERLY COST SUMMARY
Cost Category | Q1 | Q2 | Q3 | Q4 | Annual Total
Parts & Materials ($)
Labour Hours
Labour Cost ($)
Call-Out Charges ($)
Total Visit Cost ($)
Budget ($)
Variance vs Budget ($)
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Deficiency Log
Your HVAC Co. |  |  |  |  | HVAC Quarterly Maintenance Checklist
⚠️ DEFICIENCY & REMEDIAL WORKS LOG
# | Qtr | Date Found | Asset ID | Deficiency Description | Remedial Action Required | Assigned To | Due Date | Date Closed | Priority | Status
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
📊 DEFICIENCY SUMMARY
Total Deficiencies Raised: | [5 empty] | 0
Q1 Deficiencies: | [5 empty] | 0
Q2 Deficiencies: | [5 empty] | 0
Q3 Deficiencies: | [5 empty] | 0
Q4 Deficiencies: | [5 empty] | 0
Open / Unresolved: | [5 empty] | 0
Closed / Resolved: | [5 empty] | 0
Critical Priority: | [5 empty] | 0
Overdue Items: | [5 empty] | 0
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Annual KPI Summary
Your HVAC Co. |  |  |  |  | HVAC Quarterly Maintenance Checklist
📈 ANNUAL KPI & PERFORMANCE SUMMARY — FOUR-QUARTER OVERVIEW
Contract / Site: Year: Prepared By:
📊 QUARTERLY VISIT COMPLIANCE
Metric | Q1 | Q2 | Q3 | Q4 | Annual Total | Target | Status
Visits Scheduled |  |  |  |  | 0 | 4
Visits Completed |  |  |  |  | 0 | 4
Visits Missed |  |  |  |  | 0 | 0
Completion Rate (%) | [5 empty] | ≥98%
Tasks Completed |  |  |  |  | 0 | Per matrix
Tasks Failed / Defects |  |  |  |  | 0 | 0
Deficiencies Raised |  |  |  |  | 0 | 0
Deficiencies Closed |  |  |  |  | 0 | All
📊 KPI TRACKER — QUARTERLY
KPI Metric | Target | Q1 Actual | Q1 Status | Q2 Actual | Q2 Status | Q3 Actual | Q3 Status | Q4 Actual | Q4 Status
PPM Completion Rate (%) | ≥98%
First-Time Fix Rate (%) | ≥85%
Mean Time to Respond (hrs) | ≤4 hrs
Mean Time to Repair (hrs) | ≤8 hrs
System Uptime / Availability (%) | ≥99%
Open Critical Defects (count) | 0
Refrigerant Leak Events | 0
Customer Satisfaction Score | ≥4.0/5
Parts Cost vs Budget (%) | ≤100%
Reactive Call-Outs (count) | ≤2/qtr
💰 ANNUAL COST SUMMARY
Cost Category | Q1 | Q2 | Q3 | Q4 | Annual Total | Budget | Variance
Parts & Consumables ($)
Labour Cost ($)
Reactive / Call-Out ($)
Total Cost ($)
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Annual Summary & Sign-Off
Your HVAC Co. | [5 empty] | HVAC Quarterly Maintenance Checklist
HVAC QUARTERLY MAINTENANCE — ANNUAL SERVICE REPORT
Covering all four scheduled quarterly visits for the service year
📊 FOUR-QUARTER COMPLETION SUMMARY
Quarter | Visit Date | Technician | Items Checked | Pass | Fail | N/A | Defects Raised | Defects Closed | Parts Cost ($) | Status
Q1 (Jan–Mar)
Q2 (Apr–Jun)
Q3 (Jul–Sep)
Q4 (Oct–Dec)
ANNUAL TOTALS |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
📝 ANNUAL FINDINGS & RECOMMENDATIONS
⚠️ OUTSTANDING ITEMS & FOLLOW-UP ACTIONS
📋 EQUIPMENT CONDITION ASSESSMENT
System / Equipment | Condition Rating | Age (yrs) | Remaining Life (est.) | Recommended Action | Priority
✍️ ANNUAL SIGN-OFF & CLIENT ACCEPTANCE
Service Provider — Lead Technician: |  |  | Print Name: |  |  | Signature: |  |  | Date:
Service Provider — Contract Manager: |  |  | Cert / Reg #: |  |  | Company: |  |  | Phone:
Client — Building Owner / FM Manager: |  |  | Print Name: |  |  | Signature: |  |  | Date:
Client — Authorised Representative: |  |  | Title / Role: |  |  | Comments: |  |  | Date Accepted:
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com