## Cover
Your HVAC Co. | HVAC Spring Maintenance Checklist
🌿 HVAC SPRING START-UP & MAINTENANCE CHECKLIST
📋 SERVICE INFORMATION
Property / Facility Name: |  | Work Order / Service #:
Property Address: |  | Service Date:
Building Type / Use: |  | Next Service Due Date:
Owner / Contact Name: |  | Technician Name:
Owner Phone / Email: |  | Technician License #:
Equipment Location / Zone: |  | Company:
⚙️ EQUIPMENT INFORMATION
Equipment Type / Description: |  | Manufacturer:
Model Number: |  | Serial Number:
System Tag / Unit ID: |  | Refrigerant Type:
Nominal Cooling Capacity (Tons): |  | Nominal Heating Capacity (BTU/hr):
Motor HP / Drive Type: |  | Filter Type / MERV Rating:
Last Service Date: |  | Hours Since Last Service:
🌤️ SPRING SERVICE CONDITIONS
Service Start Date: |  | Weather Conditions:
Service Start Time: |  | Outdoor Temp (°F):
Service End Time: |  | Outdoor RH (%):
System Operating Mode: |  | Indoor Temp (°F):
Building Occupancy Status: |  | Barometric Pressure (in. Hg):
📝 SCOPE OF SPRING MAINTENANCE
☑ Cooling system start-up and refrigerant charge verification
☑ Coil cleaning — evaporator and condenser
☑ Filter replacement and airflow verification
☑ Electrical connections, capacitors, and safety device testing
☑ Fan, belt, motor, and bearing inspection / lubrication
☑ Thermostat / BAS setpoint changeover to cooling season
☑ Condensate system inspection and flush
☑ Performance data collection and documentation
✅ CERTIFICATION & SIGN-OFF
Certified Technician Name: |  | Signature:
License / Cert #: |  | Date:
Customer Acceptance: |  | Signature:
Customer Name / Title: |  | Date Accepted:
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Cooling System Start-Up
Your HVAC Co. |  |  |  | HVAC Spring Maintenance Checklist
❄️ COOLING SYSTEM SPRING START-UP
Checklist Item | Pass | Fail | N/A | Notes / Corrective Action
▶ PRE-START INSPECTION
Verify unit was properly shut down at end of last season | ☐ | ☐ | ☐
Remove any winter covers, debris screens, or storage items | ☐ | ☐ | ☐
Inspect unit cabinet / housing for rust, dents, or damage | ☐ | ☐ | ☐
Verify all access panels are present and fasteners are secure | ☐ | ☐ | ☐
Check for pest / rodent activity inside unit | ☐ | ☐ | ☐
Inspect refrigerant line insulation — repair or replace if damaged | ☐ | ☐ | ☐
Verify unit pad / mounting is level and structurally sound | ☐ | ☐ | ☐
Check crankcase heater — verify warm before starting (24 hrs) | ☐ | ☐ | ☐
▶ COMPRESSOR
Inspect compressor for oil stains or refrigerant leak signs | ☐ | ☐ | ☐
Check compressor electrical connections and terminals | ☐ | ☐ | ☐
Verify compressor mounting bolts are tight | ☐ | ☐ | ☐
Measure and record compressor amp draw (all phases) | ☐ | ☐ | ☐
Listen for unusual noise — knocking, chattering, or rattling | ☐ | ☐ | ☐
Verify compressor contactor — check for pitting or burning | ☐ | ☐ | ☐
Test high-pressure and low-pressure safety cutouts | ☐ | ☐ | ☐
▶ CONDENSER SECTION
Clean condenser coil — remove dirt, debris, cottonwood, leaves | ☐ | ☐ | ☐
Straighten bent condenser fins with fin comb as needed | ☐ | ☐ | ☐
Inspect condenser fan blades — clean and check for cracks | ☐ | ☐ | ☐
Verify condenser fan motor rotation direction is correct | ☐ | ☐ | ☐
Measure and record condenser fan motor amp draw | ☐ | ☐ | ☐
Lubricate condenser fan motor bearings (if applicable) | ☐ | ☐ | ☐
Clear all vegetation and debris within 24 inches of unit | ☐ | ☐ | ☐
Verify condenser coil fins are free of chemical / oxidation damage | ☐ | ☐ | ☐
▶ REFRIGERANT SYSTEM
Perform refrigerant leak check — electronic detector (all joints) | ☐ | ☐ | ☐
Measure and record suction pressure | ☐ | ☐ | ☐
Measure and record discharge / head pressure | ☐ | ☐ | ☐
Calculate and record suction superheat | ☐ | ☐ | ☐
Calculate and record liquid subcooling | ☐ | ☐ | ☐
Verify refrigerant charge — add or recover as needed | ☐ | ☐ | ☐
Document refrigerant type, quantity added/removed, EPA cert # | ☐ | ☐ | ☐
Inspect liquid line sight glass — clear with no bubbles | ☐ | ☐ | ☐
Check TXV / EEV operation — verify superheat target | ☐ | ☐ | ☐
Inspect filter drier — replace if moisture indicated | ☐ | ☐ | ☐
▶ FIRST START-UP VERIFICATION
Perform first start-up — monitor for abnormal noise or tripping | ☐ | ☐ | ☐
Verify cooling mode sequence of operation | ☐ | ☐ | ☐
Allow system to stabilize (15 min) before recording readings | ☐ | ☐ | ☐
Verify discharge air temperature achieves design setpoint | ☐ | ☐ | ☐
Record steady-state suction and discharge pressures | ☐ | ☐ | ☐
Verify unit cycles off and on correctly on thermostat call | ☐ | ☐ | ☐
Check for refrigerant or oil leaks after first run | ☐ | ☐ | ☐
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Coils, Filters & Airflow
Your HVAC Co. |  |  |  | HVAC Spring Maintenance Checklist
🌬️ COILS, FILTERS & AIR DISTRIBUTION — SPRING SERVICE
Checklist Item | Pass | Fail | N/A | Notes / Corrective Action
▶ EVAPORATOR / COOLING COIL
Inspect evaporator coil face for dirt, mold, or blockage | ☐ | ☐ | ☐
Clean evaporator coil with approved no-rinse coil cleaner | ☐ | ☐ | ☐
Rinse coil if required by cleaner instructions | ☐ | ☐ | ☐
Inspect coil fins — straighten with fin comb as needed | ☐ | ☐ | ☐
Check coil for signs of icing or freeze damage | ☐ | ☐ | ☐
Verify coil drain pan is clean, sloped, and draining freely | ☐ | ☐ | ☐
Inspect coil access panel gaskets / seals for air bypass | ☐ | ☐ | ☐
▶ CONDENSATE SYSTEM
Clean condensate drain pan — remove slime, algae, debris | ☐ | ☐ | ☐
Flush condensate drain line with water and/or algaecide tablet | ☐ | ☐ | ☐
Verify condensate trap is properly primed and seated | ☐ | ☐ | ☐
Check drain line slope, support, and termination point | ☐ | ☐ | ☐
Test condensate overflow switch / float safety | ☐ | ☐ | ☐
Verify secondary drain pan is clean and drain is open | ☐ | ☐ | ☐
Add algaecide / biocide treatment tablet to pan | ☐ | ☐ | ☐
▶ FILTER INSPECTION & REPLACEMENT
Remove and inspect all existing filters — note condition | ☐ | ☐ | ☐
Measure filter differential pressure drop (in. wg) — record | ☐ | ☐ | ☐
Replace all disposable filters with new per spec | ☐ | ☐ | ☐
Verify correct MERV rating is installed per design | ☐ | ☐ | ☐
Clean / wash permanent filters if applicable | ☐ | ☐ | ☐
Inspect filter housing and rack for bypass air leakage | ☐ | ☐ | ☐
Check filter housing seals and gaskets | ☐ | ☐ | ☐
Record filter brand, MERV rating, size, and quantity replaced | ☐ | ☐ | ☐
▶ SUPPLY & RETURN AIR DISTRIBUTION
Inspect all supply diffusers / registers — clean as needed | ☐ | ☐ | ☐
Inspect all return air grilles — clean as needed | ☐ | ☐ | ☐
Verify supply diffusers are unobstructed and properly aimed | ☐ | ☐ | ☐
Check for signs of condensation or staining at diffusers | ☐ | ☐ | ☐
Verify all grille fasteners are secure | ☐ | ☐ | ☐
Inspect accessible ductwork — check for leaks, damage, or sag | ☐ | ☐ | ☐
Check flexible duct connections for kinks or disconnections | ☐ | ☐ | ☐
Inspect duct insulation for moisture, damage, or missing sections | ☐ | ☐ | ☐
Verify outdoor air intake screen is clean and unobstructed | ☐ | ☐ | ☐
Verify exhaust fans / gravity dampers operate freely | ☐ | ☐ | ☐
▶ DAMPERS & ECONOMIZER
Inspect and exercise all balancing dampers | ☐ | ☐ | ☐
Verify smoke / fire dampers are open — fusible links intact | ☐ | ☐ | ☐
Check outside air and return air dampers — full stroke operation | ☐ | ☐ | ☐
Lubricate damper shafts and linkages as required | ☐ | ☐ | ☐
Verify economizer controls respond to OA enthalpy / temp | ☐ | ☐ | ☐
Test economizer full-open / full-close operation | ☐ | ☐ | ☐
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Fan, Motor & Electrical
Your HVAC Co. |  |  |  | HVAC Spring Maintenance Checklist
⚡ FAN, MOTOR & ELECTRICAL — SPRING SERVICE
Checklist Item | Pass | Fail | N/A | Notes / Corrective Action
▶ SUPPLY / RETURN FAN
Inspect fan wheel / blades — clean dirt buildup thoroughly | ☐ | ☐ | ☐
Check fan wheel for cracks, loose blades, or wear | ☐ | ☐ | ☐
Verify fan wheel set screws are tight | ☐ | ☐ | ☐
Inspect fan housing for rust, cracks, or debris | ☐ | ☐ | ☐
Verify fan rotation direction is correct | ☐ | ☐ | ☐
Check fan shaft for wobble or bearing play | ☐ | ☐ | ☐
Inspect flexible duct connections at fan — no tears or gaps | ☐ | ☐ | ☐
▶ BELT DRIVE SYSTEM
Inspect all belts for wear, glazing, cracking, or fraying | ☐ | ☐ | ☐
Check belt tension — adjust to manufacturer spec | ☐ | ☐ | ☐
Measure and record belt deflection | ☐ | ☐ | ☐
Inspect sheaves / pulleys for groove wear and alignment | ☐ | ☐ | ☐
Replace belt(s) if worn, glazed, or out of spec | ☐ | ☐ | ☐
Verify sheave size matches design specifications | ☐ | ☐ | ☐
Check sheave set screws and key for tightness | ☐ | ☐ | ☐
▶ MOTOR INSPECTION & LUBRICATION
Clean motor exterior — check ventilation openings are clear | ☐ | ☐ | ☐
Inspect motor for overheating signs (discoloration, odor) | ☐ | ☐ | ☐
Lubricate motor bearings per manufacturer schedule | ☐ | ☐ | ☐
Lubricate fan shaft bearings (grease fittings) | ☐ | ☐ | ☐
Measure and record motor amp draw — all phases | ☐ | ☐ | ☐
Verify amp draw is within FLA nameplate rating (<FLA) | ☐ | ☐ | ☐
Check motor mounting bolts for tightness | ☐ | ☐ | ☐
Inspect motor insulation resistance if suspected issue | ☐ | ☐ | ☐
▶ ELECTRICAL SYSTEM
Inspect main disconnect — check for heat, corrosion, or damage | ☐ | ☐ | ☐
Tighten all electrical terminal connections | ☐ | ☐ | ☐
Inspect contactors / relays — check for pitting or burning | ☐ | ☐ | ☐
Measure and record supply voltage — all phases | ☐ | ☐ | ☐
Verify phase balance (<2% unbalance) | ☐ | ☐ | ☐
Test and verify run capacitor — check µF vs. rating | ☐ | ☐ | ☐
Test and verify start capacitor (if applicable) | ☐ | ☐ | ☐
Inspect wiring insulation for damage or heat stress marks | ☐ | ☐ | ☐
Verify circuit breaker / fuse sizing matches equipment nameplate | ☐ | ☐ | ☐
Check ground connections are secure | ☐ | ☐ | ☐
▶ SAFETY & CONTROL DEVICES
Test high-pressure safety cutout — verify trip point | ☐ | ☐ | ☐
Test low-pressure safety cutout — verify trip point | ☐ | ☐ | ☐
Test freeze protection thermostat / stat | ☐ | ☐ | ☐
Test smoke / fire shutdown interlock (if applicable) | ☐ | ☐ | ☐
Test condensate overflow / float switch | ☐ | ☐ | ☐
Verify all safety switches auto-reset or manual-reset correctly | ☐ | ☐ | ☐
Test crankcase heater operation and continuity | ☐ | ☐ | ☐
▶ THERMOSTAT & BUILDING CONTROLS
Switch thermostat / BAS to COOLING season program | ☐ | ☐ | ☐
Verify cooling setpoints are correct for season | ☐ | ☐ | ☐
Verify heating setpoints are appropriate (setback mode) | ☐ | ☐ | ☐
Calibrate thermostats / temperature sensors as needed | ☐ | ☐ | ☐
Test demand control ventilation (CO₂ sensor) if applicable | ☐ | ☐ | ☐
Verify occupied / unoccupied scheduling is correct | ☐ | ☐ | ☐
Check BAS communication — all points online | ☐ | ☐ | ☐
Download and log BAS trend data — review for anomalies | ☐ | ☐ | ☐
Verify economizer lockout setpoint is set for cooling season | ☐ | ☐ | ☐
▶ VFD (VARIABLE FREQUENCY DRIVE) — IF APPLICABLE
Check VFD display — clear all fault codes, log any history | ☐ | ☐ | ☐
Clean VFD heat sink fins and internal cooling fan | ☐ | ☐ | ☐
Verify minimum and maximum Hz setpoints are correct | ☐ | ☐ | ☐
Check input and output wiring terminal tightness | ☐ | ☐ | ☐
Log VFD runtime hours | ☐ | ☐ | ☐
Test VFD manual override / bypass operation | ☐ | ☐ | ☐
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Gas Heat & Combustion
Your HVAC Co. |  |  |  | HVAC Spring Maintenance Checklist
🔥 GAS HEAT & COMBUSTION — SPRING INSPECTION & SHUTDOWN
Checklist Item | Pass | Fail | N/A | Notes / Corrective Action
▶ HEAT EXCHANGER INSPECTION
Inspect primary heat exchanger for cracks, holes, or corrosion | ☐ | ☐ | ☐
Inspect secondary heat exchanger (condensing units) | ☐ | ☐ | ☐
Check heat exchanger seams, welds, and connections | ☐ | ☐ | ☐
Perform combustion air CO test if heat exchanger is suspect | ☐ | ☐ | ☐
Inspect burners for rust, blockage, or deterioration | ☐ | ☐ | ☐
Verify burner ignition — clean igniter / flame sensor | ☐ | ☐ | ☐
Clean flame sensor rod — sand lightly to remove oxidation | ☐ | ☐ | ☐
Check draft inducer motor — spin freely, no wobble | ☐ | ☐ | ☐
▶ COMBUSTION & VENTING
Inspect flue / vent pipe for corrosion, cracks, or loose joints | ☐ | ☐ | ☐
Verify all flue joints are sealed (foil tape / PVC cement) | ☐ | ☐ | ☐
Check vent termination — clear of debris and bird nests | ☐ | ☐ | ☐
Verify combustion air intake is unobstructed | ☐ | ☐ | ☐
Test gas valve operation — open / close on call | ☐ | ☐ | ☐
Measure and record gas pressure (manifold and inlet) | ☐ | ☐ | ☐
Check gas line and connections for leaks (bubble solution) | ☐ | ☐ | ☐
Test limit switch operation and reset | ☐ | ☐ | ☐
Verify rollout switch has not tripped | ☐ | ☐ | ☐
▶ SPRING HEATING SYSTEM SHUTDOWN
Verify heating system can be safely switched to off / standby | ☐ | ☐ | ☐
Set heating setpoints to seasonal minimum per owner preference | ☐ | ☐ | ☐
Confirm heat will not activate during summer cooling season | ☐ | ☐ | ☐
Document condition of heat exchanger in service notes | ☐ | ☐ | ☐
Note any items requiring attention before fall startup | ☐ | ☐ | ☐
Advise owner of any safety concerns with combustion equipment | ☐ | ☐ | ☐
▶ ELECTRIC HEAT (IF APPLICABLE)
Inspect electric heat strips — check for burned elements | ☐ | ☐ | ☐
Measure each stage amp draw — compare to nameplate | ☐ | ☐ | ☐
Verify sequencer / staging operation | ☐ | ☐ | ☐
Check heat strip limit switches and safety cutouts | ☐ | ☐ | ☐
Inspect heat strip connections for heat damage or arcing | ☐ | ☐ | ☐
Set heat strips to lockout for summer if required | ☐ | ☐ | ☐
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Performance Data
Your HVAC Co. |  |  |  | HVAC Spring Maintenance Checklist
📊 SPRING START-UP PERFORMANCE MEASUREMENTS
Parameter | Spec / Design | Measured | Unit | Tolerance | Status | Notes
Total Supply CFM |  |  | CFM | ±10%
Total Return CFM |  |  | CFM | ±10%
Outside Air CFM |  |  | CFM | See Design
Supply Static Pressure (Ext.) |  |  | in. wg | Per Design
Filter Differential Pressure |  |  | in. wg | <Initial Drop
Fan RPM |  |  | RPM | ±5%
Motor Amp Draw — Phase A |  |  | Amps | <FLA
Motor Amp Draw — Phase B |  |  | Amps | <FLA
Motor Amp Draw — Phase C |  |  | Amps | <FLA
Supply Voltage — Phase A-B |  |  | VAC | ±5%
Supply Voltage — Phase B-C |  |  | VAC | ±5%
Supply Voltage — Phase A-C |  |  | VAC | ±5%
Run Capacitor — Measured µF |  |  | µF | ±6% of Rating
🌡️ TEMPERATURE & REFRIGERATION READINGS
Parameter | Spec / Design | Measured | Unit | Tolerance | Status | Notes
Discharge Air Temp — Cooling Mode |  |  | °F | Mfr. Spec
Return Air Temp (RAT) |  |  | °F | Per Design
Outdoor Air Temp (OAT) |  |  | °F | —
Indoor Space Temp |  |  | °F | Setpoint ±2°F
Suction Pressure |  |  | PSIG | Per Refrigerant Chart
Discharge / Head Pressure |  |  | PSIG | Per Refrigerant Chart
Suction Line Temp (Superheat) |  |  | °F | 8–12°F TXV
Liquid Line Temp (Subcooling) |  |  | °F | 10–15°F TXV
Condensing Temp (SCT) |  |  | °F | Per Chart
Evaporating Temp (SST) |  |  | °F | Per Chart
Delta-T Across Evap Coil (DB) |  |  | °F | 16–22°F
Entering Coil Temp (EAT DB) |  |  | °F | Per Design
Leaving Coil Temp (LAT DB) |  |  | °F | Per Design
Entering Coil Temp (EAT WB) |  |  | °F | Per Design
Leaving Coil Temp (LAT WB) |  |  | °F | Per Design
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Deficiency Log
Your HVAC Co. |  |  |  | HVAC Spring Maintenance Checklist
⚠️ DEFICIENCY LOG & CORRECTIVE ACTION TRACKING
# | Location / System | Deficiency Description | Corrective Action Required | Assigned To | Due Date | Date Resolved | Priority | Status
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
📊 DEFICIENCY SUMMARY
Total Deficiencies Identified: |  |  |  |  | 0
Open / Unresolved: |  |  |  |  | 0
Resolved / Closed: |  |  |  |  | 0
Critical / High Priority: |  |  |  |  | 0
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Summary & Sign-Off
Your HVAC Co. |  |  |  | HVAC Spring Maintenance Checklist
🌿 HVAC SPRING MAINTENANCE — FINAL SUMMARY & SIGN-OFF
📊 SPRING MAINTENANCE RESULTS SUMMARY
Section | Items Checked | Pass | Fail | N/A | Critical Items | Overall Status | Technician Notes
Cooling System Start-Up
Coils, Filters & Airflow
Fan, Motor & Electrical
Gas Heat & Combustion
📝 OVERALL FINDINGS & RECOMMENDATIONS
Overall Spring Start-Up Status:
Cooling System Ready for Season?:
Refrigerant Charge Status:
Critical Items Requiring Immediate Attention:
Items Deferred to Next Service:
Recommended Return Visit / Follow-Up Date:
Estimated Parts / Repair Cost:
System Efficiency Rating (1–5):
🗒️ TECHNICIAN NOTES / NARRATIVE
✍️ APPROVAL & SIGNATURE BLOCK
Service Technician: |  |  | Print Name: |  |  | Signature: |  | Date:
License / Cert #: |  |  | Expiration: |  |  | Company: |  | Phone:
Customer Acceptance: |  |  | Title: |  |  | Signature: |  | Date Accepted:
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com