## Cover
Your HVAC Co. | HVAC Fall Maintenance Checklist
🍂 HVAC FALL START-UP & MAINTENANCE CHECKLIST
📋 SERVICE INFORMATION
Property / Facility Name: |  | Work Order / Service #:
Property Address: |  | Service Date:
Building Type / Use: |  | Next Service Due Date:
Owner / Contact Name: |  | Technician Name:
Owner Phone / Email: |  | Technician License #:
Equipment Location / Zone: |  | Company:
⚙️ EQUIPMENT INFORMATION
Equipment Type / Description: |  | Manufacturer:
Model Number: |  | Serial Number:
System Tag / Unit ID: |  | Refrigerant Type:
Nominal Heating Capacity (BTU/hr): |  | Nominal Cooling Capacity (Tons):
Motor HP / Drive Type: |  | Filter Type / MERV Rating:
Last Service Date: |  | Hours Since Last Service:
🍂 FALL SERVICE CONDITIONS
Service Start Date: |  | Weather Conditions:
Service Start Time: |  | Outdoor Temp (°F):
Service End Time: |  | Outdoor RH (%):
System Operating Mode: |  | Indoor Temp (°F):
Building Occupancy Status: |  | Barometric Pressure (in. Hg):
📝 SCOPE OF FALL MAINTENANCE
☑ Heating system start-up, heat exchanger inspection, and combustion analysis
☑ Cooling system shutdown, seasonal storage, and condenser winterization
☑ Filter replacement and airflow verification
☑ Electrical connections, capacitors, and safety device testing
☑ Fan, belt, motor, and bearing inspection / lubrication
☑ Thermostat / BAS setpoint changeover to heating season
☑ Condensate system inspection and treatment
☑ Freeze protection verification (low-ambient controls, glycol, heat trace)
☑ Performance data collection and documentation
✅ CERTIFICATION & SIGN-OFF
Certified Technician Name: |  | Signature:
License / Cert #: |  | Date:
Customer Acceptance: |  | Signature:
Customer Name / Title: |  | Date Accepted:
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Heating System Start-Up
Your HVAC Co. |  |  |  | HVAC Fall Maintenance Checklist
🔥 HEATING SYSTEM FALL START-UP
Checklist Item | Pass | Fail | N/A | Notes / Corrective Action
▶ PRE-START INSPECTION
Verify unit was properly maintained at end of last heating season | ☐ | ☐ | ☐
Remove any covers, debris, or items stored near/on unit | ☐ | ☐ | ☐
Inspect unit cabinet / housing for rust, dents, or damage | ☐ | ☐ | ☐
Verify all access panels present, secured, and gaskets intact | ☐ | ☐ | ☐
Check for pest / rodent activity inside unit — clear nests | ☐ | ☐ | ☐
Inspect gas line connections for corrosion or physical damage | ☐ | ☐ | ☐
Verify unit is level and mounting is structurally sound | ☐ | ☐ | ☐
Check crankcase heater operation before first start (24 hrs on) | ☐ | ☐ | ☐
▶ GAS HEAT — FURNACE / ROOFTOP UNIT
Inspect heat exchanger for cracks, holes, rust, or deterioration | ☐ | ☐ | ☐
Perform CO test at supply registers — record reading (ppm) | ☐ | ☐ | ☐
Inspect secondary heat exchanger on condensing furnaces | ☐ | ☐ | ☐
Clean and inspect burners — remove rust scale and debris | ☐ | ☐ | ☐
Check and clean igniter / hot surface igniter (HSI) | ☐ | ☐ | ☐
Clean flame sensor rod — light sanding to remove oxidation | ☐ | ☐ | ☐
Verify gas valve opens and closes on thermostat call | ☐ | ☐ | ☐
Measure and record gas inlet pressure (in. wg) | ☐ | ☐ | ☐
Measure and record manifold gas pressure (in. wg) | ☐ | ☐ | ☐
Test primary limit switch — verify trip and reset | ☐ | ☐ | ☐
Test rollout limit switches — verify have not tripped | ☐ | ☐ | ☐
Check draft inducer motor — rotates freely, no wobble or noise | ☐ | ☐ | ☐
Inspect flue / vent pipe for corrosion, cracks, and loose joints | ☐ | ☐ | ☐
Verify all flue joints properly sealed (PVC cement / foil tape) | ☐ | ☐ | ☐
Check vent termination — unobstructed, per manufacturer clearance | ☐ | ☐ | ☐
Verify combustion air intake is unobstructed and screened | ☐ | ☐ | ☐
Perform first heating start-up — monitor closely | ☐ | ☐ | ☐
Record steady-state supply air temperature in heating mode | ☐ | ☐ | ☐
▶ HEAT PUMP — HEATING MODE (IF APPLICABLE)
Verify reversing valve switches to heating mode on thermostat call | ☐ | ☐ | ☐
Check defrost board — set defrost timer and termination temp | ☐ | ☐ | ☐
Test defrost cycle initiation and termination | ☐ | ☐ | ☐
Verify auxiliary / emergency heat energizes at correct differential | ☐ | ☐ | ☐
Check balance point control setting matches design | ☐ | ☐ | ☐
Verify crankcase heater is energized before start | ☐ | ☐ | ☐
▶ ELECTRIC HEAT (IF APPLICABLE)
Inspect all electric heat strips — check for burned elements | ☐ | ☐ | ☐
Measure and record each heat stage amp draw vs. nameplate | ☐ | ☐ | ☐
Verify heat sequencer / staging operation is correct | ☐ | ☐ | ☐
Test heat strip high-limit switches and safety cutouts | ☐ | ☐ | ☐
Inspect strip connections for arcing, heat damage, or corrosion | ☐ | ☐ | ☐
Verify heat strips de-energize when cooling is active | ☐ | ☐ | ☐
▶ HYDRONIC / HOT WATER HEAT (IF APPLICABLE)
Verify boiler / hot water system is operational | ☐ | ☐ | ☐
Check hydronic system pressure — fill to design level | ☐ | ☐ | ☐
Bleed air from radiators and terminal units | ☐ | ☐ | ☐
Verify zone valves open and close on thermostat call | ☐ | ☐ | ☐
Check expansion tank pressure and pre-charge | ☐ | ☐ | ☐
Inspect pump seals and motor for leaks or unusual noise | ☐ | ☐ | ☐
Test backflow preventer and pressure relief valve | ☐ | ☐ | ☐
Verify system glycol concentration (freeze protection %) | ☐ | ☐ | ☐
▶ FIRST HEAT START-UP VERIFICATION
Perform first start-up — monitor for abnormal noise or tripping | ☐ | ☐ | ☐
Verify heating mode sequence of operation end-to-end | ☐ | ☐ | ☐
Allow system to stabilize (15 min) before recording readings | ☐ | ☐ | ☐
Verify supply air temperature achieves design heating setpoint | ☐ | ☐ | ☐
Verify unit cycles off and on correctly on thermostat call | ☐ | ☐ | ☐
Check for gas / CO leaks after first run (electronic detector) | ☐ | ☐ | ☐
Document all as-found and as-left settings | ☐ | ☐ | ☐
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Cooling System Shutdown
Your HVAC Co. |  |  |  | HVAC Fall Maintenance Checklist
❄️ COOLING SYSTEM FALL SHUTDOWN & WINTERIZATION
Checklist Item | Pass | Fail | N/A | Notes / Corrective Action
▶ COOLING SYSTEM SHUTDOWN CHECKLIST
Verify cooling season has ended — OAT consistently below setpoint | ☐ | ☐ | ☐
Switch thermostat / BAS to HEATING season program | ☐ | ☐ | ☐
Confirm cooling will not activate during heating season | ☐ | ☐ | ☐
Document final cooling season refrigerant readings and status | ☐ | ☐ | ☐
Log any cooling issues observed during season for spring follow-up | ☐ | ☐ | ☐
▶ CONDENSER UNIT — FALL INSPECTION
Inspect condenser coil — clean cottonwood / leaf debris buildup | ☐ | ☐ | ☐
Straighten bent condenser fins as needed | ☐ | ☐ | ☐
Inspect condenser fan blades for cracks or damage | ☐ | ☐ | ☐
Check condenser fan motor wiring and connections | ☐ | ☐ | ☐
Verify refrigerant lines are insulated and secure | ☐ | ☐ | ☐
Inspect unit disconnect and electrical connections | ☐ | ☐ | ☐
Remove any vegetation or debris grown up around unit | ☐ | ☐ | ☐
Check unit pad / mounting — confirm level and stable | ☐ | ☐ | ☐
▶ REFRIGERANT SYSTEM — FALL CHECK
Check system for refrigerant leaks before shutdown season | ☐ | ☐ | ☐
Verify low-ambient controls are set for winter operation (if unit runs year-round) | ☐ | ☐ | ☐
Confirm head pressure controls are operational (if applicable) | ☐ | ☐ | ☐
Verify crankcase heater is energized for winter standby | ☐ | ☐ | ☐
Document current refrigerant pressures and charge status | ☐ | ☐ | ☐
▶ WINTERIZATION & FREEZE PROTECTION
Verify condenser unit winter cover installed (if required by mfr.) | ☐ | ☐ | ☐
Inspect and test heat trace on condensate lines (if installed) | ☐ | ☐ | ☐
Verify drain pans are clean and condensate lines won't freeze | ☐ | ☐ | ☐
Confirm freeze protection thermostat setpoint is correct | ☐ | ☐ | ☐
Test freeze stat — verify fan shutoff operates | ☐ | ☐ | ☐
Verify glycol concentration in chilled water loop (if applicable) | ☐ | ☐ | ☐
Blow out / drain condensate lines in unheated spaces | ☐ | ☐ | ☐
Check pipe insulation in mechanical rooms / exterior chases | ☐ | ☐ | ☐
▶ EVAPORATIVE COOLER / SWAMP COOLER SHUTDOWN (IF APPLICABLE)
Shut off water supply to evaporative cooler | ☐ | ☐ | ☐
Drain and flush water distribution pan | ☐ | ☐ | ☐
Remove and clean water distribution pads or media | ☐ | ☐ | ☐
Lubricate water pump and motor bearings | ☐ | ☐ | ☐
Install winter cover / block register to prevent cold air infiltration | ☐ | ☐ | ☐
Inspect float valve and water supply line — shut off and drain | ☐ | ☐ | ☐
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Filters, Coils & Airflow
Your HVAC Co. |  |  |  | HVAC Fall Maintenance Checklist
🌬️ FILTERS, COILS & AIR DISTRIBUTION — FALL SERVICE
Checklist Item | Pass | Fail | N/A | Notes / Corrective Action
▶ FILTER INSPECTION & REPLACEMENT
Remove and inspect all existing filters — note condition | ☐ | ☐ | ☐
Measure filter differential pressure drop (in. wg) — record | ☐ | ☐ | ☐
Replace all disposable filters per schedule / spec | ☐ | ☐ | ☐
Verify correct MERV rating installed per design | ☐ | ☐ | ☐
Clean / wash permanent filters if applicable | ☐ | ☐ | ☐
Inspect filter housing and rack for bypass air leakage | ☐ | ☐ | ☐
Check filter housing seals and gaskets for deterioration | ☐ | ☐ | ☐
Record filter brand, MERV rating, size, and quantity replaced | ☐ | ☐ | ☐
▶ HEATING COIL / HEAT EXCHANGER
Inspect heating coil face for fouling or blockage | ☐ | ☐ | ☐
Clean heating coil with approved cleaner if fouled | ☐ | ☐ | ☐
Check coil fins for damage — straighten as needed | ☐ | ☐ | ☐
Inspect electric heat strips for burned elements | ☐ | ☐ | ☐
Verify coil / heat strip connections are tight | ☐ | ☐ | ☐
▶ EVAPORATOR / COOLING COIL
Inspect evaporator coil face for mold, mildew, or fouling | ☐ | ☐ | ☐
Clean coil with approved cleaner if required | ☐ | ☐ | ☐
Verify coil drain pan is clean and drains properly | ☐ | ☐ | ☐
Check for signs of moisture / condensation issues from cooling season | ☐ | ☐ | ☐
▶ CONDENSATE SYSTEM — FALL TREATMENT
Clean condensate drain pan — remove algae, slime, and debris | ☐ | ☐ | ☐
Flush condensate drain line with water and/or biocide | ☐ | ☐ | ☐
Verify condensate trap is properly primed | ☐ | ☐ | ☐
Check drain line slope and termination — clear any blockages | ☐ | ☐ | ☐
Add algaecide / biocide treatment tablet to drain pan | ☐ | ☐ | ☐
Verify condensate overflow switch operates correctly | ☐ | ☐ | ☐
Winterize condensate drain in unheated spaces as required | ☐ | ☐ | ☐
▶ SUPPLY & RETURN AIR DISTRIBUTION
Inspect all supply diffusers / registers — clean as needed | ☐ | ☐ | ☐
Inspect all return air grilles — clean as needed | ☐ | ☐ | ☐
Verify supply diffusers are unobstructed | ☐ | ☐ | ☐
Check for signs of moisture staining at diffusers / ceiling tiles | ☐ | ☐ | ☐
Verify all grille fasteners are secure | ☐ | ☐ | ☐
Inspect accessible ductwork — check for leaks or disconnections | ☐ | ☐ | ☐
Check flexible duct connections — no kinks or tears | ☐ | ☐ | ☐
Verify outdoor air intake is screened and unobstructed | ☐ | ☐ | ☐
Check exhaust fans and gravity dampers operate freely | ☐ | ☐ | ☐
▶ DAMPERS & ECONOMIZER — FALL SETTING
Verify economizer controls respond to outdoor air conditions | ☐ | ☐ | ☐
Set economizer low-limit (heating season lockout) per design | ☐ | ☐ | ☐
Inspect and exercise all balancing dampers | ☐ | ☐ | ☐
Verify smoke / fire dampers are open — fusible links intact | ☐ | ☐ | ☐
Check outside air and return air dampers — full stroke | ☐ | ☐ | ☐
Lubricate damper shafts and linkages as required | ☐ | ☐ | ☐
Verify minimum outside air damper position meets ventilation code | ☐ | ☐ | ☐
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Fan, Motor & Electrical
Your HVAC Co. |  |  |  | HVAC Fall Maintenance Checklist
⚡ FAN, MOTOR & ELECTRICAL — FALL SERVICE
Checklist Item | Pass | Fail | N/A | Notes / Corrective Action
▶ SUPPLY / RETURN FAN
Inspect fan wheel / blades — clean dirt buildup thoroughly | ☐ | ☐ | ☐
Check fan wheel for cracks, loose blades, or wear | ☐ | ☐ | ☐
Verify fan wheel set screws are tight | ☐ | ☐ | ☐
Inspect fan housing for rust, cracks, or debris accumulation | ☐ | ☐ | ☐
Verify fan rotation direction is correct | ☐ | ☐ | ☐
Check fan shaft for wobble or bearing play | ☐ | ☐ | ☐
Inspect flexible duct connections at fan — no tears or gaps | ☐ | ☐ | ☐
▶ BELT DRIVE SYSTEM
Inspect all belts for wear, glazing, cracking, or fraying | ☐ | ☐ | ☐
Check belt tension — adjust to manufacturer specification | ☐ | ☐ | ☐
Measure and record belt deflection | ☐ | ☐ | ☐
Inspect sheaves / pulleys for groove wear and alignment | ☐ | ☐ | ☐
Replace belt(s) if worn, glazed, or out of spec | ☐ | ☐ | ☐
Verify sheave sizes match design specifications | ☐ | ☐ | ☐
Check sheave set screws and key for tightness | ☐ | ☐ | ☐
▶ MOTOR INSPECTION & LUBRICATION
Clean motor exterior — check ventilation openings are clear | ☐ | ☐ | ☐
Inspect motor for overheating signs (discoloration, odor) | ☐ | ☐ | ☐
Lubricate motor bearings per manufacturer schedule | ☐ | ☐ | ☐
Lubricate fan shaft bearings (grease fittings) | ☐ | ☐ | ☐
Measure and record motor amp draw — all phases | ☐ | ☐ | ☐
Verify amp draw is within FLA nameplate rating | ☐ | ☐ | ☐
Check motor mounting bolts for tightness | ☐ | ☐ | ☐
▶ ELECTRICAL SYSTEM
Inspect main disconnect — check for heat, corrosion, or damage | ☐ | ☐ | ☐
Tighten all electrical terminal connections | ☐ | ☐ | ☐
Inspect contactors / relays — check for pitting or burning | ☐ | ☐ | ☐
Measure and record supply voltage — all phases | ☐ | ☐ | ☐
Verify phase balance (<2% unbalance) | ☐ | ☐ | ☐
Test and verify run capacitor — check µF vs. rating | ☐ | ☐ | ☐
Test and verify start capacitor (if applicable) | ☐ | ☐ | ☐
Inspect wiring insulation for damage or heat stress marks | ☐ | ☐ | ☐
Verify circuit breaker / fuse sizing matches equipment nameplate | ☐ | ☐ | ☐
Check ground connections are secure and undamaged | ☐ | ☐ | ☐
▶ SAFETY & CONTROL DEVICES
Test high-pressure safety cutout — verify trip point | ☐ | ☐ | ☐
Test low-pressure / low-ambient safety cutout | ☐ | ☐ | ☐
Test freeze protection thermostat — verify fan shutoff | ☐ | ☐ | ☐
Test smoke / fire shutdown interlock (if applicable) | ☐ | ☐ | ☐
Test condensate overflow / float switch | ☐ | ☐ | ☐
Verify all safety switches reset properly (auto and manual) | ☐ | ☐ | ☐
Check crankcase heater — verify energized and warm | ☐ | ☐ | ☐
▶ THERMOSTAT & BUILDING CONTROLS — FALL CHANGEOVER
Switch thermostat / BAS to HEATING season program | ☐ | ☐ | ☐
Verify heating setpoints are correct for season | ☐ | ☐ | ☐
Verify cooling setpoints are in appropriate setback / lockout mode | ☐ | ☐ | ☐
Calibrate thermostats / temperature sensors as needed | ☐ | ☐ | ☐
Set morning warm-up routine in BAS schedule | ☐ | ☐ | ☐
Verify night setback temperatures are correct for heating season | ☐ | ☐ | ☐
Test demand control ventilation (CO₂ sensor) if applicable | ☐ | ☐ | ☐
Verify occupied / unoccupied scheduling is correct for season | ☐ | ☐ | ☐
Check BAS communication — all points responding | ☐ | ☐ | ☐
Download and log BAS trend data — review summer season anomalies | ☐ | ☐ | ☐
Verify economizer heating-season lockout setpoint is set | ☐ | ☐ | ☐
▶ VFD (VARIABLE FREQUENCY DRIVE) — IF APPLICABLE
Check VFD display — clear fault codes, log fault history | ☐ | ☐ | ☐
Clean VFD heat sink fins and internal cooling fan | ☐ | ☐ | ☐
Verify minimum and maximum Hz setpoints for heating season | ☐ | ☐ | ☐
Check input and output wiring terminal tightness | ☐ | ☐ | ☐
Log VFD runtime hours — compare to last service | ☐ | ☐ | ☐
Test VFD manual override / bypass operation | ☐ | ☐ | ☐
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Freeze Protection
Your HVAC Co. |  |  |  | HVAC Fall Maintenance Checklist
🧊 FREEZE PROTECTION & WINTERIZATION
Checklist Item | Pass | Fail | N/A | Notes / Corrective Action
▶ LOW-AMBIENT CONTROLS
Verify low-ambient head pressure control kit is installed / operational | ☐ | ☐ | ☐
Set condenser fan cycling control for winter operation | ☐ | ☐ | ☐
Verify crankcase heater is energized on all compressors | ☐ | ☐ | ☐
Test low-ambient lockout control — verify cooling disabled below setpoint | ☐ | ☐ | ☐
Check variable speed condenser fan drive settings (if applicable) | ☐ | ☐ | ☐
▶ PIPE FREEZE PROTECTION
Inspect all exposed refrigerant line insulation — repair or replace | ☐ | ☐ | ☐
Inspect and test heat trace cables on exposed piping | ☐ | ☐ | ☐
Verify heat trace thermostat setpoint is set above freeze threshold | ☐ | ☐ | ☐
Check pipe insulation in unconditioned mechanical rooms and chases | ☐ | ☐ | ☐
Verify all drain lines in unheated spaces are insulated or heat traced | ☐ | ☐ | ☐
Confirm chilled water loop is drained OR glycol-protected | ☐ | ☐ | ☐
Test glycol concentration — verify adequate for minimum winter OAT | ☐ | ☐ | ☐
Inspect glycol system for corrosion inhibitor level | ☐ | ☐ | ☐
▶ CONDENSATE FREEZE PROTECTION
Inspect condensate drain line routing through unconditioned spaces | ☐ | ☐ | ☐
Install heat trace on condensate lines where freeze risk exists | ☐ | ☐ | ☐
Verify condensate lines pitch correctly to drain — no standing water | ☐ | ☐ | ☐
Blow out condensate lines in areas where system will not run in winter | ☐ | ☐ | ☐
Check condensate pan for standing water — drain completely | ☐ | ☐ | ☐
▶ OUTDOOR EQUIPMENT WINTERIZATION
Inspect outdoor unit coil guard / hail guard for damage | ☐ | ☐ | ☐
Remove leaves, cottonwood, and debris from inside condenser | ☐ | ☐ | ☐
Check condenser base pan drain hole is unobstructed | ☐ | ☐ | ☐
Install approved manufacturer winter cover if unit will not run | ☐ | ☐ | ☐
Verify unit disconnect is accessible and labeled | ☐ | ☐ | ☐
Check refrigerant line set where it enters building — seal any gaps | ☐ | ☐ | ☐
Document unit condition and any concerns for spring start-up | ☐ | ☐ | ☐
▶ HUMIDIFICATION SYSTEM — FALL STARTUP (IF APPLICABLE)
Inspect humidifier water supply line and valve | ☐ | ☐ | ☐
Clean humidifier scale pan and water distribution components | ☐ | ☐ | ☐
Replace evaporative humidifier pad / media | ☐ | ☐ | ☐
Test humidifier operation — verify output on call from humidistat | ☐ | ☐ | ☐
Set humidistat to heating season setpoint (typically 30–40% RH) | ☐ | ☐ | ☐
Check humidifier drain and overflow path is clear | ☐ | ☐ | ☐
Verify steam humidifier canister condition (replace if scaled) | ☐ | ☐ | ☐
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Performance Data
Your HVAC Co. |  |  |  | HVAC Fall Maintenance Checklist
📊 FALL START-UP PERFORMANCE MEASUREMENTS
Parameter | Spec / Design | Measured | Unit | Tolerance | Status | Notes
Total Supply CFM |  |  | CFM | ±10%
Total Return CFM |  |  | CFM | ±10%
Outside Air CFM |  |  | CFM | See Design
Supply Static Pressure (Ext.) |  |  | in. wg | Per Design
Filter Differential Pressure |  |  | in. wg | <Clean Drop
Fan RPM |  |  | RPM | ±5%
Motor Amp Draw — Phase A |  |  | Amps | <FLA
Motor Amp Draw — Phase B |  |  | Amps | <FLA
Motor Amp Draw — Phase C |  |  | Amps | <FLA
Supply Voltage — Phase A-B |  |  | VAC | ±5%
Supply Voltage — Phase B-C |  |  | VAC | ±5%
Supply Voltage — Phase A-C |  |  | VAC | ±5%
Run Capacitor — Measured µF |  |  | µF | ±6% of Rating
🌡️ TEMPERATURE & HEATING PERFORMANCE READINGS
Parameter | Spec / Design | Measured | Unit | Tolerance | Status | Notes
Supply Air Temp — Heating Mode |  |  | °F | Per Design
Return Air Temp (RAT) |  |  | °F | Per Design
Outdoor Air Temp (OAT) |  |  | °F | —
Indoor Space Temp |  |  | °F | Setpoint ±2°F
Temperature Rise Across Heat Exchanger |  |  | °F | Mfr. Spec
Gas Inlet Pressure |  |  | in. wg | Per Mfr.
Gas Manifold Pressure |  |  | in. wg | Per Mfr.
CO at Supply Register (Heating Mode) |  |  | ppm | <9 ppm
Delta-T Across Electric Heat Strips |  |  | °F | Per Staging
Hot Water Supply Temp (Hydronic) |  |  | °F | Per Design
Hot Water Return Temp (Hydronic) |  |  | °F | Per Design
Glycol Concentration (Freeze Protection) |  |  | % vol | Per Climate Zone
Humidifier Output / RH Setpoint |  |  | %RH | 30–40% RH
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Combustion Analysis
Your HVAC Co. |  |  |  | HVAC Fall Maintenance Checklist
🔬 COMBUSTION ANALYSIS & GAS HEAT DATA
Parameter | Spec / Design | Measured | Unit | Acceptable Range | Status | Notes
Gas Type |  |  |  | Natural Gas / Propane
Gas Inlet Pressure |  |  | in. wg | 5–7 NG / 11–13 LP
Gas Manifold Pressure |  |  | in. wg | Per Mfr. Nameplate
Flue Gas Temperature — Gross |  |  | °F | Per Mfr.
Flue Gas Temperature — Net |  |  | °F | Per Mfr.
CO₂ in Flue Gas |  |  | % vol | 8–10% NG / 10–12% LP
O₂ in Flue Gas |  |  | % vol | 4–8% typical
CO in Flue Gas (undiluted) |  |  | ppm | <400 ppm
CO at Supply Register (air-free) |  |  | ppm | <9 ppm ASHRAE
Combustion Efficiency |  |  | % | >80% typical
Excess Air |  |  | % | 10–30% typical
Draft Pressure (Over-Fire) |  |  | in. wg | Per Mfr.
Draft Pressure (Flue) |  |  | in. wg | Per Mfr.
Flame Sensor Current |  |  | µA | >1.5 µA
Temperature Rise Across HX |  |  | °F | Per Mfr. Nameplate
Burner Ignition Time |  |  | sec | <4 sec typical
⚠️ HEAT EXCHANGER INSPECTION RECORD
Inspection Point | Method | Finding | Pass | Fail | N/A | Corrective Action / Notes
Primary heat exchanger — visual inspection | Visual |  | ☐ | ☐ | ☐
Primary heat exchanger — CO test at registers | CO Analyzer |  | ☐ | ☐ | ☐
Heat exchanger seams and welds | Visual / Light |  | ☐ | ☐ | ☐
Secondary heat exchanger (condensing furnace) | Visual |  | ☐ | ☐ | ☐
Burner compartment — rust / scale / debris | Visual |  | ☐ | ☐ | ☐
Flue collector box — cracks or rust | Visual |  | ☐ | ☐ | ☐
Induced draft motor and housing | Visual / Manual |  | ☐ | ☐ | ☐
Vent connector pipe — all joints | Visual |  | ☐ | ☐ | ☐
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Deficiency Log
Your HVAC Co. |  |  |  | HVAC Fall Maintenance Checklist
⚠️ DEFICIENCY LOG & CORRECTIVE ACTION TRACKING
# | Location / System | Deficiency Description | Corrective Action Required | Assigned To | Due Date | Date Resolved | Priority | Status
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
📊 DEFICIENCY SUMMARY
Total Deficiencies Identified: |  |  |  |  | 0
Open / Unresolved: |  |  |  |  | 0
Resolved / Closed: |  |  |  |  | 0
Critical / High Priority: |  |  |  |  | 0
Safety-Related Items: |  |  |  |  | 0
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com

## Summary & Sign-Off
Your HVAC Co. |  |  |  | HVAC Fall Maintenance Checklist
🍂 HVAC FALL MAINTENANCE — FINAL SUMMARY & SIGN-OFF
📊 FALL MAINTENANCE RESULTS SUMMARY
Section | Items Checked | Pass | Fail | N/A | Critical Items | Overall Status | Technician Notes
Heating System Start-Up
Cooling System Shutdown
Filters, Coils & Airflow
Fan, Motor & Electrical
Freeze Protection
📝 OVERALL FINDINGS & RECOMMENDATIONS
Overall Fall Start-Up Status:
Heating System Ready for Season?:
Heat Exchanger / Combustion Safety Status:
CO Test Result (ppm at register):
Freeze Protection Status:
Cooling System Properly Shutdown?:
Critical Items Requiring Immediate Attention:
Items Deferred to Spring Service:
Recommended Return Visit / Follow-Up Date:
System Overall Condition Rating (1–5):
🗒️ TECHNICIAN NOTES / NARRATIVE
✍️ APPROVAL & SIGNATURE BLOCK
Service Technician: |  |  | Print Name: |  |  | Signature: |  | Date:
License / Cert #: |  |  | Expiration: |  |  | Company: |  | Phone:
Customer Acceptance: |  |  | Title: |  |  | Signature: |  | Date Accepted:
Your HVAC Co. • Rogers, AR • (479) 555-0100 • www.yourhvacco.com