## PM Checklist
Your HVAC Co. |  |  |  | COMMERCIAL PREVENTIVE MAINTENANCE CHECKLIST
Rogers, AR • (555) 867-5309 • www.yourhvac.com • service@yourhvac.com
📋 SERVICE ORDER INFORMATION
Customer / Company Name:
Service Address:
City / State / ZIP:
Site Contact Name:
Site Contact Phone:
Contract / PO Number:
Service Date:
Next PM Due Date:
Technician Name:
Tech Cert # / EPA 608:
Dispatch Ticket #:
🏭 EQUIPMENT IDENTIFICATION
Equipment Tag | Mfr / Model | Serial # | Refrigerant Type | Tonnage / Capacity | Install Year | Location / Zone
⚠️ SECTION 1 — SAFETY & SITE PREPARATION
# | Inspection Item / Task | Pass | Fail | N/A | Measured Value | Notes / Corrective Action
1 | Reviewed MSDS/SDS sheets for refrigerants and chemicals on site | ☐ | ☐ | ☐
2 | Verified lockout/tagout (LOTO) procedures completed before service | ☐ | ☐ | ☐
3 | Confirmed PPE donned: gloves, safety glasses, arc flash rated (if applicable) | ☐ | ☐ | ☐
4 | Inspected ladder(s) and fall protection equipment — no defects | ☐ | ☐ | ☐
5 | Identified emergency shut-off locations with site contact | ☐ | ☐ | ☐
6 | Confirmed confined space entry permit (if applicable) obtained | ☐ | ☐ | ☐
7 | Reviewed equipment history/previous PM notes before starting | ☐ | ☐ | ☐
8 | Photographed unit nameplate and pre-service condition | ☐ | ☐ | ☐
💨 SECTION 2 — AIR HANDLING UNIT (AHU) / FAN COIL UNIT
# | Inspection Item / Task | Pass | Fail | N/A | Measured Value | Notes / Corrective Action
▸ Filters & Airflow
1 | Inspect and record filter condition (note MERV rating) | ☐ | ☐ | ☐
2 | Replace filters — document qty, size, and MERV rating | ☐ | ☐ | ☐
3 | Check filter rack for bypass gaps and seal if present | ☐ | ☐ | ☐
4 | Measure and record return air static pressure (in. w.c.) | ☐ | ☐ | ☐
5 | Measure and record supply air static pressure (in. w.c.) | ☐ | ☐ | ☐
6 | Verify supply / return CFM within 10% of design spec | ☐ | ☐ | ☐
▸ Coil & Drain Pan
7 | Inspect evaporator coil for dirt, biological growth, or damage | ☐ | ☐ | ☐
8 | Clean evaporator coil with approved coil cleaner — no foaming agent left | ☐ | ☐ | ☐
9 | Flush and inspect condensate drain pan — no standing water or algae | ☐ | ☐ | ☐
10 | Clear condensate drain line — flush with diluted bleach or biocide | ☐ | ☐ | ☐
11 | Confirm condensate drain P-trap is intact and properly sized | ☐ | ☐ | ☐
12 | Inspect coil fins — straighten if bent (>10% fin damage = note for replacement) | ☐ | ☐ | ☐
▸ Blower & Drive
13 | Inspect blower wheel for dirt buildup — clean if needed | ☐ | ☐ | ☐
14 | Check blower motor amperage — record and compare to FLA nameplate | ☐ | ☐ | ☐
15 | Inspect belt(s) for wear, cracking, or glazing — replace if needed | ☐ | ☐ | ☐
16 | Measure and record belt tension (deflection method) | ☐ | ☐ | ☐
17 | Lubricate motor and blower bearings (if applicable — grease-type only) | ☐ | ☐ | ☐
18 | Verify blower RPM within spec; check for vibration or noise | ☐ | ☐ | ☐
19 | Inspect VFD (if equipped) — check fault log, clean filters, check airflow | ☐ | ☐ | ☐
▸ Controls & Safeties
20 | Test smoke detector / fire/smoke damper (if installed) — document result | ☐ | ☐ | ☐
21 | Verify low-limit freeze stat set point and operation | ☐ | ☐ | ☐
22 | Test high-temperature limit switch | ☐ | ☐ | ☐
23 | Confirm outdoor air damper opens/closes per schedule | ☐ | ☐ | ☐
24 | Verify economizer operation (if equipped) — free cooling enabled properly | ☐ | ☐ | ☐
25 | Inspect all ductwork connections at AHU — seal leaks with mastic or UL-181 tape | ☐ | ☐ | ☐
🔩 SECTION 3 — CONDENSING UNIT / COMPRESSOR
# | Inspection Item / Task | Pass | Fail | N/A | Measured Value | Notes / Corrective Action
▸ Condenser Coil & Fan
1 | Inspect condenser coil for damage, restrictions, or fouling | ☐ | ☐ | ☐
2 | Clean condenser coil with low-pressure water spray (top-down); log any damage | ☐ | ☐ | ☐
3 | Inspect condenser fan blades for damage or imbalance | ☐ | ☐ | ☐
4 | Measure condenser fan motor amperage — record vs. FLA nameplate | ☐ | ☐ | ☐
5 | Lubricate condenser fan motors (if applicable) | ☐ | ☐ | ☐
6 | Verify condenser fan rotation direction is correct | ☐ | ☐ | ☐
7 | Inspect and tighten condenser fan blade set screws | ☐ | ☐ | ☐
8 | Check condenser fan guards / protective screens — secure and intact | ☐ | ☐ | ☐
▸ Compressor Inspection
9 | Listen for unusual compressor noise (knocking, slugging, squealing) | ☐ | ☐ | ☐
10 | Measure and record compressor RLA vs. nameplate FLA | ☐ | ☐ | ☐
11 | Inspect compressor terminals for corrosion, heat marks, or loose connections | ☐ | ☐ | ☐
12 | Check crankcase heater operation (if equipped) — verify heat output | ☐ | ☐ | ☐
13 | Inspect compressor vibration isolators — replace if cracked or collapsed | ☐ | ☐ | ☐
14 | Check for oil stains indicating refrigerant/oil leak at compressor base | ☐ | ☐ | ☐
🧊 SECTION 4 — REFRIGERATION SYSTEM INSPECTION
# | Inspection Item / Task | Pass | Fail | N/A | Measured Value | Notes / Corrective Action
1 | Perform full leak check — manifold gauge, electronic detector, UV dye (if present) | ☐ | ☐ | ☐
2 | Record suction pressure (psig) and corresponding saturated suction temp (°F) | ☐ | ☐ | ☐
3 | Record discharge pressure (psig) and corresponding saturated discharge temp (°F) | ☐ | ☐ | ☐
4 | Calculate and record superheat at evaporator | ☐ | ☐ | ☐
5 | Calculate and record subcooling at condenser outlet | ☐ | ☐ | ☐
6 | Verify superheat within spec (TXV: 8–12°F / Fixed orifice: 10–20°F typical) | ☐ | ☐ | ☐
7 | Verify subcooling within spec (TXV: 10–15°F typical) | ☐ | ☐ | ☐
8 | Inspect refrigerant sight glass — clear, no bubbles (if equipped) | ☐ | ☐ | ☐
9 | Inspect liquid line filter/drier — note pressure drop if gauge ports present | ☐ | ☐ | ☐
10 | Check refrigerant charge — document refrigerant type and amount (lbs.) on file | ☐ | ☐ | ☐
11 | Inspect all refrigerant piping for insulation integrity and UV damage | ☐ | ☐ | ☐
12 | Verify service valves are fully open — core depressors seated | ☐ | ☐ | ☐
⚡ SECTION 5 — ELECTRICAL SYSTEM INSPECTION
# | Inspection Item / Task | Pass | Fail | N/A | Measured Value | Notes / Corrective Action
1 | Verify supply voltage at unit — record L1-L2, L1-L3, L2-L3 (V) | ☐ | ☐ | ☐
2 | Check for voltage imbalance — must not exceed 2% (NEMA MG1) | ☐ | ☐ | ☐
3 | Inspect and tighten all electrical connections (contactor, terminals, wire lugs) | ☐ | ☐ | ☐
4 | Inspect contactors — check for pitting, arcing, or sticking; replace if needed | ☐ | ☐ | ☐
5 | Test capacitors — measure uF vs. rated (acceptable: ±6% tolerance) | ☐ | ☐ | ☐
6 | Inspect wiring for insulation damage, overheating marks, or rodent damage | ☐ | ☐ | ☐
7 | Test and document fuse continuity / breaker ratings | ☐ | ☐ | ☐
8 | Verify all disconnect ratings match unit nameplate requirements | ☐ | ☐ | ☐
9 | Inspect control board — look for burn marks, swollen capacitors, fault codes | ☐ | ☐ | ☐
10 | Verify ground connections are solid and bonded to equipment chassis | ☐ | ☐ | ☐
11 | Document and clear all active fault codes from control board | ☐ | ☐ | ☐
12 | Test time delay relay / crankcase heater delay (if applicable) | ☐ | ☐ | ☐
🔥 SECTION 6 — HEATING SYSTEM INSPECTION (GAS / ELECTRIC / HEAT PUMP)
# | Inspection Item / Task | Pass | Fail | N/A | Measured Value | Notes / Corrective Action
▸ Gas Heat
1 | Inspect heat exchanger for cracks, holes, or corrosion (use mirror/camera) | ☐ | ☐ | ☐
2 | Verify burner flames — stable blue flame; no yellow tips or lifting | ☐ | ☐ | ☐
3 | Measure and record gas manifold pressure (in. w.c.) | ☐ | ☐ | ☐
4 | Measure and record incoming gas supply pressure (in. w.c.) | ☐ | ☐ | ☐
5 | Test gas valve operation — opens/closes reliably on thermostat call | ☐ | ☐ | ☐
6 | Inspect and clean burner assembly — remove corrosion and debris | ☐ | ☐ | ☐
7 | Test igniter (hot surface or spark) — verify reliable ignition in ≤3 tries | ☐ | ☐ | ☐
8 | Test flame sensor — clean with fine steel wool; measure µA (min 1.5 µA) | ☐ | ☐ | ☐
9 | Inspect flue venting — no blockages, proper slope, no rust perforation | ☐ | ☐ | ☐
10 | Test rollout safety switches and high-limit switch | ☐ | ☐ | ☐
11 | Measure supply air temperature rise — verify within design range (°F) | ☐ | ☐ | ☐
▸ Electric Heat / Heat Pump Supplemental Heat
12 | Inspect electric heat elements — no open coils or discoloration | ☐ | ☐ | ☐
13 | Measure strip heat amperage vs. rated KW | ☐ | ☐ | ☐
14 | Test sequencers — verify staged operation | ☐ | ☐ | ☐
15 | Inspect heat pump defrost board and defrost termination thermostat | ☐ | ☐ | ☐
16 | Verify balance point / auxiliary heat lockout is set per design | ☐ | ☐ | ☐
17 | Test emergency heat mode — confirm strips energize directly | ☐ | ☐ | ☐
🖥️ SECTION 7 — CONTROLS, THERMOSTAT & BAS/BMS
# | Inspection Item / Task | Pass | Fail | N/A | Measured Value | Notes / Corrective Action
1 | Verify thermostat/controller set points (cooling, heating, humidity, CO2) | ☐ | ☐ | ☐
2 | Inspect thermostat wiring — no loose connections or chafed insulation | ☐ | ☐ | ☐
3 | Test occupied / unoccupied scheduling mode transitions | ☐ | ☐ | ☐
4 | Verify demand control ventilation (DCV) sensor operation (CO2 range: 400–1100 ppm) | ☐ | ☐ | ☐
5 | Confirm BAS/BMS point mapping is accurate — check for ghost faults | ☐ | ☐ | ☐
6 | Test all zone dampers — open/close on command from controller | ☐ | ☐ | ☐
7 | Calibrate supply and return air temperature sensors (±1°F tolerance) | ☐ | ☐ | ☐
8 | Calibrate humidity sensor (if equipped) — verify with handheld reference | ☐ | ☐ | ☐
9 | Test economizer / free-cooling enable/disable from BAS | ☐ | ☐ | ☐
10 | Review alarm log in BAS — document and address all critical alarms | ☐ | ☐ | ☐
11 | Verify remote monitoring connectivity — check data transmission to cloud or server | ☐ | ☐ | ☐
12 | Test manual override functions from BAS for each AHU/RTU | ☐ | ☐ | ☐
🏗️ SECTION 8 — STRUCTURAL, PHYSICAL & GENERAL CONDITION
# | Inspection Item / Task | Pass | Fail | N/A | Measured Value | Notes / Corrective Action
1 | Inspect unit cabinet / casing — dents, corrosion, missing panels | ☐ | ☐ | ☐
2 | Verify access panels are in place and secure; screws present | ☐ | ☐ | ☐
3 | Inspect unit curb / roof curb — no rust-through, standing water, or separation | ☐ | ☐ | ☐
4 | Verify unit is level — adjust leveling feet or shim if needed | ☐ | ☐ | ☐
5 | Inspect vibration isolators / spring mounts — replace if degraded | ☐ | ☐ | ☐
6 | Inspect refrigerant and drain line hangers — secure, no sagging | ☐ | ☐ | ☐
7 | Inspect refrigerant line insulation — repair any exposed copper | ☐ | ☐ | ☐
8 | Verify unit clearances meet manufacturer minimums on all sides | ☐ | ☐ | ☐
9 | Check for bird/pest nesting inside unit — remove and treat | ☐ | ☐ | ☐
10 | Inspect rooftop penetrations and flashing for leaks | ☐ | ☐ | ☐
11 | Document overall unit condition rating: Excellent / Good / Fair / Poor | ☐ | ☐ | ☐
12 | Photograph any deficiencies found during inspection | ☐ | ☐ | ☐
📊 SECTION 9 — MEASURED DATA LOG
Parameter | Measured Value | Unit | Design / Spec | Status | Notes
Supply Air Temp (Cooling) |  | °F | Per design schedule
Return Air Temp |  | °F | Per design schedule
Supply Air Temp (Heating) |  | °F | Depends on setpoint
Temperature Rise (Gas) |  | °F | Mfr. spec ±5°F
Suction Pressure |  | psig | Varies by refrigerant
Discharge Pressure |  | psig | Varies by refrigerant
Suction Sat. Temp |  | °F | Varies by refrigerant
Discharge Sat. Temp |  | °F | Varies by refrigerant
Superheat (evap outlet) |  | °F | TXV: 8–12 / Orifice: 10–20
Subcooling (cond. outlet) |  | °F | 10–15°F typical
Supply Static Pressure |  | in. w.c. | Per design schedule
Return Static Pressure |  | in. w.c. | Per design schedule
Total External Static |  | in. w.c. | Per design schedule
Supply CFM (measured) |  | CFM | Per design schedule
Outdoor Air CFM |  | CFM | Per design schedule
CO2 Level (return air) |  | ppm | ≤ 1100 ppm ASHRAE 62.1
Relative Humidity (supply) |  | %RH | 40–60% RH (ASHRAE 55)
Voltage L1-L2 |  | VAC | ±10% of nameplate
Voltage L1-L3 |  | VAC | ±10% of nameplate
Voltage L2-L3 |  | VAC | ±10% of nameplate
Voltage Imbalance |  | % | < 2% (NEMA MG1)
Compressor RLA |  | Amps | Nameplate FLA
Condenser Fan Amps |  | Amps | Nameplate FLA
Blower Motor Amps |  | Amps | Nameplate FLA
Capacitor (compressor) |  | µF | Nameplate ±6%
Capacitor (fan motor) |  | µF | Nameplate ±6%
Flame Sensor Signal |  | µA | ≥ 1.5 µA
Gas Manifold Pressure |  | in. w.c. | Mfr. spec
Refrigerant Type |  | — | Per nameplate
Refrigerant Added (lbs.) |  | lbs. | Document per EPA 608
📝 SECTION 10 — FINDINGS, RECOMMENDATIONS & SIGN-OFF
Deficiencies / Immediate Safety Concerns:
Recommended Repairs (next 30 days):
Long-Term Recommendations (next PM cycle):
Parts Used During This Service (part # / qty / description):
Technician Signature:
Customer / Site Contact Signature:
Overall PM Result: |  |  | ☐ Complete — No Issues ☐ Complete — Issues Noted ☐ Incomplete — Return Visit Required
Your HVAC Co. • Rogers, AR • (555) 867-5309 • www.yourhvac.com • EPA 608 Universal • NATE Certified

## Quick Reference
Your HVAC Co. |  |  |  | PM QUICK REFERENCE GUIDE
Rogers, AR • (555) 867-5309 • www.yourhvac.com
🧊 REFRIGERANT PRESSURE-TEMPERATURE QUICK REFERENCE
Refrigerant | Evap Temp (°F) | Suction (psig) | Cond Temp (°F) | Discharge (psig) | Superheat Target | Subcooling Target
R-410A | 45°F | 120 psig | 130°F | 417 psig | 8–12°F (TXV) | 10–15°F
R-22 | 45°F | 69 psig | 130°F | 260 psig | 10–18°F (TXV) | 10–15°F
R-407C | 45°F | 92 psig | 130°F | 290 psig | 8–12°F (TXV) | 10–15°F
R-32 | 45°F | 136 psig | 130°F | 446 psig | 5–10°F (TXV) | 5–10°F
R-454B | 45°F | 121 psig | 130°F | 395 psig | 8–12°F (TXV) | 10–15°F
⚡ PRO TIPS FOR MAXIMUM PM QUALITY & EFFICIENCY
1 | Always review equipment history before starting — know what the last tech found.
2 | Photograph every deficiency. Before-and-after photos reduce callback disputes.
3 | Record actual measured data — not just Pass/Fail. Data trends catch failures early.
4 | Verify voltage imbalance before leaving. >2% imbalance shortens compressor life dramatically.
5 | Clean coils top-down (condenser) and bottom-up (evaporator) for best results.
6 | Never skip the condensate drain flush — it is the most common commercial callback cause.
7 | Check capacitors with a capacitance meter, not just a multimeter. Replace if >±6% of rating.
8 | Superheat and subcooling tell you more than pressure alone — always calculate both.
9 | Log refrigerant added per EPA Section 608 requirements. Never guess or estimate.
10 | Leave the customer a copy of the completed checklist — it builds trust and justifies PM contracts.
Your HVAC Co. • Rogers, AR • (555) 867-5309 • www.yourhvac.com • EPA 608 Universal • NATE Certified