## Project Info & Equipment
Your HVAC Co. |  |  |  | HVAC EQUIPMENT COMMISSIONING CHECKLIST
Rogers, AR • (555) 867-5309 • www.yourhvac.com • service@yourhvac.com
📋 SECTION 1 — PROJECT & JOB SITE INFORMATION
Project Name / Description:
Project Number / Job Number:
Project Address:
City / State / ZIP:
Building Owner / Client Name:
Owner Contact Name & Phone:
Owner Contact Email:
General Contractor:
GC Contact Name & Phone:
Mechanical Contractor:
Mechanical Contact Name & Phone:
Commissioning Authority (CxA):
CxA Contact Name & Phone:
Engineer of Record (EOR):
EOR Contact Name & Phone:
Controls / BAS Contractor:
Controls Contact Name & Phone:
Building Type / Occupancy:
Applicable Codes & Standards:
ASHRAE Guideline 1.1 / LEED Cx: (Y/N):
Project Start Date:
Substantial Completion Date:
Commissioning Start Date:
Commissioning Completion Target:
Report / Submittal Due Date:
🏭 SECTION 2 — COMMISSIONED EQUIPMENT REGISTER
Unit Tag | Equipment Type | Manufacturer | Model Number | Serial Number | Tonnage / Capacity | Design CFM / GPM | Location / Zone | Cx Status
☐ Pending ☐ In Progress ☐ Complete
☐ Pending ☐ In Progress ☐ Complete
☐ Pending ☐ In Progress ☐ Complete
☐ Pending ☐ In Progress ☐ Complete
☐ Pending ☐ In Progress ☐ Complete
☐ Pending ☐ In Progress ☐ Complete
☐ Pending ☐ In Progress ☐ Complete
☐ Pending ☐ In Progress ☐ Complete
☐ Pending ☐ In Progress ☐ Complete
☐ Pending ☐ In Progress ☐ Complete
☐ Pending ☐ In Progress ☐ Complete
☐ Pending ☐ In Progress ☐ Complete
☐ Pending ☐ In Progress ☐ Complete
☐ Pending ☐ In Progress ☐ Complete
☐ Pending ☐ In Progress ☐ Complete
☐ Pending ☐ In Progress ☐ Complete
☐ Pending ☐ In Progress ☐ Complete
☐ Pending ☐ In Progress ☐ Complete
☐ Pending ☐ In Progress ☐ Complete
☐ Pending ☐ In Progress ☐ Complete
☐ Pending ☐ In Progress ☐ Complete
☐ Pending ☐ In Progress ☐ Complete
☐ Pending ☐ In Progress ☐ Complete
☐ Pending ☐ In Progress ☐ Complete
☐ Pending ☐ In Progress ☐ Complete
☐ Pending ☐ In Progress ☐ Complete
☐ Pending ☐ In Progress ☐ Complete
☐ Pending ☐ In Progress ☐ Complete
☐ Pending ☐ In Progress ☐ Complete
☐ Pending ☐ In Progress ☐ Complete
📁 SECTION 3 — SUBMITTAL & DESIGN DOCUMENT LOG
Document Title | Spec Section / Drawing # | Rev # | Date Received | Reviewed By | Status | Notes
Equipment Submittals (AHU, RTU, FCU, Chillers) |  |  |  |  | ☐ Approved ☐ Revise ☐ Pending
Controls / BAS Submittals & Point List |  |  |  |  | ☐ Approved ☐ Revise ☐ Pending
Sequence of Operations (SOO) |  |  |  |  | ☐ Approved ☐ Revise ☐ Pending
Mechanical Drawings (Floor Plans, Sections) |  |  |  |  | ☐ Approved ☐ Revise ☐ Pending
Electrical One-Line Diagram |  |  |  |  | ☐ Approved ☐ Revise ☐ Pending
Test & Balance (TAB) Report |  |  |  |  | ☐ Approved ☐ Revise ☐ Pending
Operation & Maintenance (O&M) Manuals |  |  |  |  | ☐ Approved ☐ Revise ☐ Pending
Prefunctional Checklist (PFC) — All Units |  |  |  |  | ☐ Approved ☐ Revise ☐ Pending
Functional Performance Test (FPT) Procedures |  |  |  |  | ☐ Approved ☐ Revise ☐ Pending
Owner Training Plan |  |  |  |  | ☐ Approved ☐ Revise ☐ Pending
Commissioning Plan |  |  |  |  | ☐ Approved ☐ Revise ☐ Pending
Cx Issues / Deficiency Log |  |  |  |  | ☐ Approved ☐ Revise ☐ Pending
Final Commissioning Report |  |  |  |  | ☐ Approved ☐ Revise ☐ Pending
LEED Cx Documentation (if applicable) |  |  |  |  | ☐ Approved ☐ Revise ☐ Pending
Your HVAC Co. • Rogers, AR • (555) 867-5309 • www.yourhvac.com • EPA 608 Universal • NATE Certified

## Prefunctional Checklist
Your HVAC Co. |  |  |  | PREFUNCTIONAL CHECKLIST (PFC) — PRE-STARTUP VERIFICATION
Rogers, AR • (555) 867-5309 • www.yourhvac.com • service@yourhvac.com
🔍 PFC HEADER — COMPLETE BEFORE STARTUP
Unit Tag / Equipment ID:
Equipment Type:
Manufacturer / Model:
Serial Number:
Installation Location / Zone:
Contractor Performing PFC:
Contractor Technician Name:
PFC Date:
Witnessed By (CxA / Engineer):
Witness Date:
🔩 PFC-A — MECHANICAL INSTALLATION VERIFICATION
# | Commissioning Task / Verification Point | Pass | Fail | N/A | Measured / Observed Value | Engineer / Tech Notes
1 | Unit installed per manufacturer's recommendations and project drawings | ☐ | ☐ | ☐
2 | Adequate service clearances maintained on all sides (per mfr. spec) | ☐ | ☐ | ☐
3 | Unit is level — verified with digital level (±0.5° tolerance) | ☐ | ☐ | ☐
4 | Vibration isolators / spring mounts installed and adjusted correctly | ☐ | ☐ | ☐
5 | Flexible duct connectors installed at unit supply and return connections | ☐ | ☐ | ☐
6 | All refrigerant piping connections made and visually inspected for leaks | ☐ | ☐ | ☐
7 | Refrigerant piping insulated and properly supported — no sags or contact with structure | ☐ | ☐ | ☐
8 | Condensate drain piping sloped correctly (1/8 in./ft. minimum toward drain) | ☐ | ☐ | ☐
9 | Condensate P-trap installed and properly sized per unit static pressure | ☐ | ☐ | ☐
10 | Condensate overflow sensor installed (if required by spec or local code) | ☐ | ☐ | ☐
11 | All ductwork connections at unit secured — no gaps; mastic or UL-181 tape applied | ☐ | ☐ | ☐
12 | Supply and return air plenums balanced and clear of debris | ☐ | ☐ | ☐
13 | Outdoor air intake screened and positioned away from exhaust discharge | ☐ | ☐ | ☐
14 | Gas piping installed, pressure tested, and approved by AHJ (gas units) | ☐ | ☐ | ☐
15 | Unit shipping brackets, blocks, and restraints removed | ☐ | ☐ | ☐
16 | All access panels, doors, and fasteners in place | ☐ | ☐ | ☐
17 | Unit nameplate readable and photographed for record | ☐ | ☐ | ☐
18 | Roof curb / structural support inspected and approved (rooftop units) | ☐ | ☐ | ☐
⚡ PFC-B — ELECTRICAL INSTALLATION VERIFICATION
# | Commissioning Task / Verification Point | Pass | Fail | N/A | Measured / Observed Value | Engineer / Tech Notes
1 | Electrical disconnect installed within sight of unit per NEC 440.14 | ☐ | ☐ | ☐
2 | Disconnect ampacity and voltage rating match unit nameplate requirements | ☐ | ☐ | ☐
3 | Supply wiring sized correctly per NEC and equipment nameplate MCA rating | ☐ | ☐ | ☐
4 | Overcurrent protection (fuse / breaker) sized per MOCP on nameplate | ☐ | ☐ | ☐
5 | Ground conductor installed and bonded to equipment chassis | ☐ | ☐ | ☐
6 | All high-voltage terminal connections torqued to spec — no loose lugs | ☐ | ☐ | ☐
7 | All low-voltage / control wiring connections verified at terminal block | ☐ | ☐ | ☐
8 | Supply voltage verified at unit disconnect (all phases): record L1-L2, L1-L3, L2-L3 | ☐ | ☐ | ☐
9 | Voltage imbalance calculated — must not exceed 2% (NEMA MG1) | ☐ | ☐ | ☐
10 | Crankcase heater installed, wired, and energized ≥24 hours before startup | ☐ | ☐ | ☐
11 | VFD (if applicable) installed, wired, and programmed per submittal | ☐ | ☐ | ☐
12 | Low-voltage control wiring shielded and separated from high-voltage conductors | ☐ | ☐ | ☐
13 | All conduit fittings, junction boxes, and covers secured | ☐ | ☐ | ☐
14 | Electrical panel circuit labeled and documented in panel schedule | ☐ | ☐ | ☐
🖥️ PFC-C — CONTROLS & BAS INSTALLATION VERIFICATION
# | Commissioning Task / Verification Point | Pass | Fail | N/A | Measured / Observed Value | Engineer / Tech Notes
1 | Thermostat / controller installed at correct height and location per plans | ☐ | ☐ | ☐
2 | Controller wiring terminated correctly and confirmed with loop check | ☐ | ☐ | ☐
3 | BAS/DDC controller programmed with sequence of operations (SOO) | ☐ | ☐ | ☐
4 | All BAS points mapped and confirmed with point-to-point checkout sheet | ☐ | ☐ | ☐
5 | Temperature sensors (supply, return, outdoor) installed at correct locations | ☐ | ☐ | ☐
6 | Temperature sensors calibrated and verified against NIST-traceable reference | ☐ | ☐ | ☐
7 | Humidity sensors installed and verified (if applicable) | ☐ | ☐ | ☐
8 | CO2 sensors installed at correct height in return air or zone (if DCV) | ☐ | ☐ | ☐
9 | Occupancy / lighting override inputs wired and verified (if applicable) | ☐ | ☐ | ☐
10 | Economizer / outdoor air damper actuator installed and wired | ☐ | ☐ | ☐
11 | Zone dampers and VAV boxes installed, wired, and actuators confirmed | ☐ | ☐ | ☐
12 | Smoke detectors in air stream installed and connected to AHU interlock | ☐ | ☐ | ☐
13 | Fire / smoke damper end switches wired and monitored by BAS | ☐ | ☐ | ☐
14 | Emergency stop (E-stop) interlock wired and tested | ☐ | ☐ | ☐
15 | BAS graphics built and reviewed with owner prior to startup | ☐ | ☐ | ☐
🔄 PFC-D — REFRIGERANT & HYDRONIC SYSTEM VERIFICATION
# | Commissioning Task / Verification Point | Pass | Fail | N/A | Measured / Observed Value | Engineer / Tech Notes
1 | Refrigerant type confirmed matches unit nameplate (document type and quantity) | ☐ | ☐ | ☐
2 | System pressure-tested per ASHRAE 15 / manufacturer spec before charging | ☐ | ☐ | ☐
3 | System leak-checked with electronic detector after charging — no leaks found | ☐ | ☐ | ☐
4 | Refrigerant charge documented (lbs.) per EPA Section 608 requirements | ☐ | ☐ | ☐
5 | Filter/drier installed and oriented correctly (arrow toward compressor) | ☐ | ☐ | ☐
6 | Sight glass installed and clear (no bubbles) after full charge | ☐ | ☐ | ☐
7 | Service valves fully open and caps torqued | ☐ | ☐ | ☐
8 | Chilled/hot water piping connected, flushed, and pressure tested (hydronic systems) | ☐ | ☐ | ☐
9 | Flow-balancing valves installed at each terminal unit (hydronic systems) | ☐ | ☐ | ☐
10 | Air purged from hydronic system — no air in coils or piping | ☐ | ☐ | ☐
11 | Chemical treatment / glycol mix verified in hydronic system (if applicable) | ☐ | ☐ | ☐
✍️ PFC SIGN-OFF — CONTRACTOR & CxA CERTIFICATION
Mechanical Contractor Representative:
Signature / Date:
Electrical Contractor Representative:
Signature / Date:
Controls Contractor Representative:
Signature / Date:
Commissioning Authority (CxA):
CxA Signature / Date:
PFC Result: |  |  | ☐ Approved — Ready for Startup ☐ Conditional — Items Noted ☐ Not Approved — Rework Required
Your HVAC Co. • Rogers, AR • (555) 867-5309 • www.yourhvac.com • EPA 608 Universal • NATE Certified

## Functional Performance Tests
Your HVAC Co. |  |  |  | FUNCTIONAL PERFORMANCE TEST (FPT) — STARTUP & VERIFICATION
Rogers, AR • (555) 867-5309 • www.yourhvac.com • service@yourhvac.com
⚙️ FPT HEADER — COMPLETE AT EACH TEST SESSION
Unit Tag / Equipment ID:
Test Date:
Outdoor Air Temp at Test (°F):
Outdoor RH at Test (%):
Technician Name & Cert #:
CxA / Witness Name:
BAS Online & Monitoring? (Y/N):
TAB Report Referenced? (Y/N):
Previous PFC Approved? (Y/N):
Deficiencies Carried In From PFC:
🚀 FPT-1 — INITIAL STARTUP SEQUENCE
# | Commissioning Task / Verification Point | Pass | Fail | N/A | Measured / Observed Value | Engineer / Tech Notes
1 | Confirmed all PFC items approved before energizing unit | ☐ | ☐ | ☐
2 | Energized unit at disconnect — no tripped breakers, blown fuses, or fault codes | ☐ | ☐ | ☐
3 | Verified crankcase heater was energized for minimum 24 hours prior to compressor start | ☐ | ☐ | ☐
4 | Initiated first start — unit powered up without nuisance trip or alarm | ☐ | ☐ | ☐
5 | Verified correct fan rotation direction (all fans — supply, return, condenser, exhaust) | ☐ | ☐ | ☐
6 | Checked for unusual vibration, noise, or mechanical interference on startup | ☐ | ☐ | ☐
7 | Verified all access panels closed and secured before startup | ☐ | ☐ | ☐
8 | Unit completed first full cooling cycle without fault | ☐ | ☐ | ☐
9 | Unit completed first full heating cycle without fault (gas / electric / heat pump) | ☐ | ☐ | ☐
10 | Defrost cycle tested (heat pump units) — initiated and terminated correctly | ☐ | ☐ | ☐
11 | Emergency shut-down tested — unit de-energized immediately on E-stop signal | ☐ | ☐ | ☐
12 | Unit restarted after E-stop — confirmed normal operation resumes correctly | ☐ | ☐ | ☐
❄️ FPT-2 — COOLING MODE FUNCTIONAL TESTS
▸ Cooling Sequence & Staged Operation
# | Commissioning Task / Verification Point | Pass | Fail | N/A | Measured / Observed Value | Engineer / Tech Notes
1 | Thermostat / controller commanded to cooling mode — unit responds within set delay | ☐ | ☐ | ☐
2 | First stage cooling initiated — compressor 1 and associated fans energize | ☐ | ☐ | ☐
3 | Second stage cooling initiated (if applicable) — compressor 2 or additional circuit energizes | ☐ | ☐ | ☐
4 | Verified supply air temperature drops to within 2°F of setpoint at steady state | ☐ | ☐ | ☐
5 | Verified condenser fans stage on/off correctly with outdoor air temp changes | ☐ | ☐ | ☐
6 | High-pressure switch tested — compressor de-energized on trip; alarm generated in BAS | ☐ | ☐ | ☐
7 | Low-pressure switch tested — compressor de-energized on trip; alarm generated in BAS | ☐ | ☐ | ☐
8 | Anti-short-cycle timer tested — compressor will not restart within 3–5 minutes | ☐ | ☐ | ☐
9 | Cooling lockout below outdoor air temp setpoint verified (if programmed) | ☐ | ☐ | ☐
10 | Satisfied cooling call — unit returned to standby without fault or alarm | ☐ | ☐ | ☐
▸ Economizer / Free Cooling (if applicable)
# | Commissioning Task / Verification Point | Pass | Fail | N/A | Measured / Observed Value | Engineer / Tech Notes
1 | Economizer enabled when outdoor conditions within enthalpy / dry-bulb limits | ☐ | ☐ | ☐
2 | Outdoor air damper opens to minimum position on unit startup | ☐ | ☐ | ☐
3 | Damper drives to full open when economizer call is active | ☐ | ☐ | ☐
4 | Damper returns to minimum position when economizer is disabled | ☐ | ☐ | ☐
5 | Economizer integrated with mechanical cooling — stages correctly without simultaneous full capacity | ☐ | ☐ | ☐
6 | High-limit control strategy verified (dry-bulb or enthalpy sensor checked against reference) | ☐ | ☐ | ☐
7 | Economizer fault / position feedback alarm tested in BAS | ☐ | ☐ | ☐
🔥 FPT-3 — HEATING MODE FUNCTIONAL TESTS
▸ Gas Heat Sequence
# | Commissioning Task / Verification Point | Pass | Fail | N/A | Measured / Observed Value | Engineer / Tech Notes
1 | Thermostat / controller commanded to heating — induced draft fan (IDF) pre-purges | ☐ | ☐ | ☐
2 | Gas valve opens; ignition sequence initiates — flame established within 3 attempts | ☐ | ☐ | ☐
3 | Flame sensor confirms burner ignition — µA reading recorded | ☐ | ☐ | ☐
4 | Supply air temperature rises to within 5°F of heating setpoint at steady state | ☐ | ☐ | ☐
5 | High-limit switch tested — burners de-energized on trip; IDF continues to purge | ☐ | ☐ | ☐
6 | Rollout safety switch tested — unit locks out and alarm generated in BAS | ☐ | ☐ | ☐
7 | Pressure switch (IDF / inducer) tested — heating will not initiate if switch fails open | ☐ | ☐ | ☐
8 | Satisfied heating call — burners extinguish; IDF post-purges and shuts down | ☐ | ☐ | ☐
9 | Gas leak check performed after heating cycle — no leaks detected | ☐ | ☐ | ☐
▸ Electric Heat / Heat Pump Auxiliary Heat
# | Commissioning Task / Verification Point | Pass | Fail | N/A | Measured / Observed Value | Engineer / Tech Notes
1 | Electric heat elements staged on sequentially — no simultaneous full-load inrush | ☐ | ☐ | ☐
2 | Supply air temperature rises to setpoint — all stages verified | ☐ | ☐ | ☐
3 | Auxiliary heat lockout temperature programmed and verified (heat pump units) | ☐ | ☐ | ☐
4 | Emergency heat mode tested — mechanical cooling locked out, all strip heat stages enabled | ☐ | ☐ | ☐
5 | High-limit thermal cutout tested on electric elements — fault and BAS alarm verified | ☐ | ☐ | ☐
6 | Heat pump defrost cycle initiated and terminated correctly — auxiliary heat energizes during defrost | ☐ | ☐ | ☐
7 | Balance point control verified — auxiliary stages based on outdoor temp (if applicable) | ☐ | ☐ | ☐
💨 FPT-4 — VENTILATION, IAQ & OUTDOOR AIR VERIFICATION
# | Commissioning Task / Verification Point | Pass | Fail | N/A | Measured / Observed Value | Engineer / Tech Notes
1 | Outdoor air damper opens to minimum position on unit start (occupied mode) | ☐ | ☐ | ☐
2 | Minimum OA CFM measured and verified within ±10% of design (ASHRAE 62.1) | ☐ | ☐ | ☐
3 | CO2 DCV tested — OA damper modulates open as CO2 level rises above setpoint | ☐ | ☐ | ☐
4 | CO2 DCV tested — OA damper returns to minimum as zone CO2 drops to setpoint | ☐ | ☐ | ☐
5 | CO2 sensor span-calibrated against NIST-traceable reference (400–2000 ppm range) | ☐ | ☐ | ☐
6 | Outdoor air damper closes fully in unoccupied mode — verified with sensor | ☐ | ☐ | ☐
7 | Morning warm-up / cool-down cycle: OA damper remains closed until space at setpoint | ☐ | ☐ | ☐
8 | Exhaust / return air ratio balanced — building pressurization slightly positive | ☐ | ☐ | ☐
9 | Building static pressure measured and documented (slight positive = 0.02–0.05 in. w.c.) | ☐ | ☐ | ☐
10 | Demand-controlled exhaust verified (if applicable — kitchen, parking, lab) | ☐ | ☐ | ☐
🖥️ FPT-5 — BAS / DDC CONTROLS FUNCTIONAL VERIFICATION
# | Commissioning Task / Verification Point | Pass | Fail | N/A | Measured / Observed Value | Engineer / Tech Notes
1 | All BAS points reading correctly — no stale, bad, or offline points | ☐ | ☐ | ☐
2 | Occupied / unoccupied schedule tested — unit transitions correctly at programmed times | ☐ | ☐ | ☐
3 | Holiday schedule tested — unit transitions to unoccupied on programmed holiday dates | ☐ | ☐ | ☐
4 | Manual BAS override tested — forced occupied mode holds for programmed duration then releases | ☐ | ☐ | ☐
5 | Supply air temperature setpoint reset verified (if SAT reset strategy specified) | ☐ | ☐ | ☐
6 | Static pressure setpoint reset verified (if VAV system with duct static reset strategy) | ☐ | ☐ | ☐
7 | All critical alarms tested: high / low temp, equipment fault, comm failure, sensor failure | ☐ | ☐ | ☐
8 | Alarm notification tested — BAS sends email/text alert to designated recipients | ☐ | ☐ | ☐
9 | Trending active for all critical points (SAT, RAT, OAT, static pressure, kW, runtime) | ☐ | ☐ | ☐
10 | BAS data historian retaining trend data correctly — verified with spot check | ☐ | ☐ | ☐
11 | Remote access to BAS from owner workstation verified | ☐ | ☐ | ☐
12 | All graphics reviewed and accepted by owner / facilities manager | ☐ | ☐ | ☐
⚠️ FPT-6 — SAFETY INTERLOCK & ALARM VERIFICATION
# | Commissioning Task / Verification Point | Pass | Fail | N/A | Measured / Observed Value | Engineer / Tech Notes
1 | Smoke detector in supply air stream tested — unit shuts down and BAS alarm generated | ☐ | ☐ | ☐
2 | Fire / smoke damper end switch tested — BAS confirms damper position | ☐ | ☐ | ☐
3 | Low-limit freeze stat tested (AHU units) — unit shuts down and alarm generated | ☐ | ☐ | ☐
4 | High discharge temperature limit tested — compressor de-energized, alarm in BAS | ☐ | ☐ | ☐
5 | Loss-of-communication (LOC) fail-safe mode tested — unit assumes safe default state | ☐ | ☐ | ☐
6 | Power failure / power restoration sequence tested — unit restarts in correct mode | ☐ | ☐ | ☐
7 | Dirty filter alarm (if differential pressure switch installed) tested | ☐ | ☐ | ☐
8 | Condensate overflow sensor tested — unit shuts down on high condensate level | ☐ | ☐ | ☐
9 | Phase failure / phase reversal protection tested (3-phase units — if equipped) | ☐ | ☐ | ☐
10 | Ground fault protection (GFCI / equipment ground fault) verified | ☐ | ☐ | ☐
✍️ FPT SIGN-OFF — TEST CERTIFICATION
Mechanical Technician:
Signature / Date:
Controls Technician:
Signature / Date:
Commissioning Authority (CxA):
CxA Signature / Date:
Owner / Facilities Representative:
Signature / Date:
FPT Overall Result: |  |  | ☐ Pass — All Tests Successful ☐ Conditional Pass — Issues Noted ☐ Fail — Re-test Required
Your HVAC Co. • Rogers, AR • (555) 867-5309 • www.yourhvac.com • EPA 608 Universal • NATE Certified

## Measured Data & TAB
Your HVAC Co. |  |  |  | COMMISSIONING MEASURED DATA & TAB VERIFICATION
Rogers, AR • (555) 867-5309 • www.yourhvac.com • service@yourhvac.com
🧊 SECTION A — REFRIGERANT SYSTEM MEASURED DATA
Parameter | Design / Spec | Measured Value | Unit | Tolerance | Status | Notes
Refrigerant Type | Per nameplate |  | — | Exact match
Total Charge (lbs.) | Per nameplate |  | lbs. | Per mfr.
Suction Pressure | Varies by ref. |  | psig | Per chart
Discharge Pressure | Varies by ref. |  | psig | Per chart
Saturated Suction Temp | Varies by ref. |  | °F | Per chart
Saturated Discharge Temp | Varies by ref. |  | °F | Per chart
Evaporator Superheat | 8–12°F (TXV) |  | °F | ±2°F
Condenser Subcooling | 10–15°F |  | °F | ±2°F
Suction Line Temp (actual) | Per design |  | °F | ±3°F
Liquid Line Temp (actual) | Per design |  | °F | ±3°F
Compressor Discharge Temp | < 225°F typical |  | °F | < 225°F
Compressor RLA | Per nameplate FLA |  | Amps | ≤ nameplate
Condenser Fan Amps (each) | Per nameplate FLA |  | Amps | ≤ nameplate
Evaporator Coil Delta-T | 16–22°F typical |  | °F | Per design
💨 SECTION B — AIRSIDE PERFORMANCE & TAB VERIFICATION
Parameter | Design Value | TAB Report Value | Field Verified | Unit | % Deviation | Status
Total Supply CFM |  |  |  | CFM
Total Return CFM |  |  |  | CFM
Outdoor Air CFM (min.) |  |  |  | CFM
Exhaust Air CFM |  |  |  | CFM
Supply Static Pressure |  |  |  | in. w.c.
Return Static Pressure |  |  |  | in. w.c.
Total External Static |  |  |  | in. w.c.
Blower RPM |  |  |  | RPM
Blower Motor Amps |  |  |  | Amps
Supply Air Temp (cooling) |  |  |  | °F
Supply Air Temp (heating) |  |  |  | °F
Return Air Temp |  |  |  | °F
Mixed Air Temp |  |  |  | °F
Outdoor Air Temp at Test |  |  |  | °F
Space Temp at Test (avg.) |  |  |  | °F
Space RH at Test (avg.) |  |  |  | %RH
Building Static Pressure | 0.02–0.05 in. w.c. |  |  | in. w.c.
CO2 — Return Air |  |  |  | ppm
CO2 — Outdoor Air (ref.) | 400–450 ppm |  |  | ppm
Zone 1 Supply CFM |  |  |  | CFM
Zone 2 Supply CFM |  |  |  | CFM
Zone 3 Supply CFM |  |  |  | CFM
Zone 4 Supply CFM |  |  |  | CFM
Zone 5 Supply CFM |  |  |  | CFM
⚡ SECTION C — ELECTRICAL PERFORMANCE DATA
Parameter | Nameplate / Spec | Measured Value | Unit | Tolerance | Status | Notes
Voltage L1-L2 | Per nameplate ±10% |  | VAC | ±10%
Voltage L1-L3 | Per nameplate ±10% |  | VAC | ±10%
Voltage L2-L3 | Per nameplate ±10% |  | VAC | ±10%
Voltage Imbalance | < 2% (NEMA MG1) |  | % | < 2%
Compressor Amps (RLA) | Per nameplate |  | Amps | ≤ nameplate
Supply Fan Amps | Per nameplate FLA |  | Amps | ≤ nameplate
Return/Exhaust Fan Amps | Per nameplate FLA |  | Amps | ≤ nameplate
Condenser Fan Amps | Per nameplate FLA |  | Amps | ≤ nameplate
Total Unit Amps (all loads) | Per nameplate MCA |  | Amps | ≤ MCA
Compressor Capacitor (µF) | Nameplate ±6% |  | µF | ±6%
Fan Motor Capacitor (µF) | Nameplate ±6% |  | µF | ±6%
VFD Output Frequency | Per BAS command |  | Hz | ±0.5 Hz
VFD Output Amps | Per design load |  | Amps | Per design
Flame Sensor Signal | ≥ 1.5 µA |  | µA | ≥ 1.5 µA
Gas Manifold Pressure | Per mfr. spec |  | in. w.c. | Per mfr.
💧 SECTION D — HYDRONIC SYSTEM DATA (if applicable)
Parameter | Design / Spec | Measured Value | Unit | Tolerance | Status | Notes
Chilled Water Supply Temp | 44–46°F typical |  | °F | ±2°F
Chilled Water Return Temp | 54–56°F typical |  | °F | Per design delta-T
CHW Delta-T | Per design |  | °F | ±1°F of design
Chilled Water Flow Rate (GPM) | Per design |  | GPM | ±10%
CHW Coil Entering Water Temp | Per design |  | °F | Per design
CHW Coil Leaving Water Temp | Per design |  | °F | Per design
Hot Water Supply Temp | Per design |  | °F | ±5°F
Hot Water Return Temp | Per design |  | °F | Per design delta-T
HW Flow Rate (GPM) | Per design |  | GPM | ±10%
System Static Pressure (fill) | Per design |  | psig | Per design
Glycol Concentration (%) | Per spec |  | % | Per spec
Your HVAC Co. • Rogers, AR • (555) 867-5309 • www.yourhvac.com • EPA 608 Universal • NATE Certified

## Issues Log & Closeout
Your HVAC Co. |  |  |  | Cx ISSUES LOG, PUNCH LIST & PROJECT CLOSEOUT
Rogers, AR • (555) 867-5309 • www.yourhvac.com • service@yourhvac.com
⚠️ SECTION A — COMMISSIONING ISSUES & DEFICIENCY LOG
Issue # | Date Found | Description of Deficiency | Found By | Responsible Party | Target Resolution | Status
1 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
2 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
3 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
4 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
5 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
6 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
7 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
8 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
9 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
10 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
11 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
12 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
13 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
14 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
15 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
16 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
17 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
18 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
19 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
20 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
21 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
22 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
23 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
24 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
25 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
26 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
27 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
28 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
29 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
30 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
31 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
32 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
33 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
34 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
35 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
36 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
37 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
38 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
39 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
40 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Owner Accept
🎓 SECTION B — OWNER / OPERATOR TRAINING LOG
Training Topic | Date | Trainer Name | Attendees | Duration (hrs) | Materials Provided | Sign-Off
System Overview & Design Intent | [5 empty] | ☐ Complete
BAS / DDC Interface & Graphics Navigation | [5 empty] | ☐ Complete
Thermostat / Zone Controller Operation | [5 empty] | ☐ Complete
Occupied / Unoccupied Scheduling | [5 empty] | ☐ Complete
Economizer & Outdoor Air Controls | [5 empty] | ☐ Complete
Filter Replacement Procedures | [5 empty] | ☐ Complete
Condensate Drain Maintenance | [5 empty] | ☐ Complete
Refrigerant Awareness & Safety | [5 empty] | ☐ Complete
Heating System Operation (Gas / Electric) | [5 empty] | ☐ Complete
Emergency Shutdown Procedures | [5 empty] | ☐ Complete
Troubleshooting Common Faults | [5 empty] | ☐ Complete
O&M Manual Review & Document Location | [5 empty] | ☐ Complete
📦 SECTION C — CLOSEOUT DELIVERABLES CHECKLIST
Deliverable | Responsible Party | Due Date | Date Submitted | Accepted By | Status | Notes
Final Commissioning Report (draft for review) |  |  |  |  | ☐ Pending ☐ Submitted ☐ Accepted
Final Commissioning Report (owner-accepted) |  |  |  |  | ☐ Pending ☐ Submitted ☐ Accepted
Signed Prefunctional Checklists (all units) |  |  |  |  | ☐ Pending ☐ Submitted ☐ Accepted
Signed Functional Performance Test Reports (all units) |  |  |  |  | ☐ Pending ☐ Submitted ☐ Accepted
Commissioning Issues / Deficiency Log (resolved) |  |  |  |  | ☐ Pending ☐ Submitted ☐ Accepted
Test & Balance (TAB) Report (final) |  |  |  |  | ☐ Pending ☐ Submitted ☐ Accepted
As-Built Mechanical Drawings |  |  |  |  | ☐ Pending ☐ Submitted ☐ Accepted
As-Built Electrical / Controls Drawings |  |  |  |  | ☐ Pending ☐ Submitted ☐ Accepted
As-Built BAS Point List & Sequences |  |  |  |  | ☐ Pending ☐ Submitted ☐ Accepted
O&M Manuals (all equipment — digital + hard copy) |  |  |  |  | ☐ Pending ☐ Submitted ☐ Accepted
Warranty Documentation (all major equipment) |  |  |  |  | ☐ Pending ☐ Submitted ☐ Accepted
Spare Parts / Attic Stock (delivered to owner) |  |  |  |  | ☐ Pending ☐ Submitted ☐ Accepted
Filter Inventory Handoff (spare filters on site) |  |  |  |  | ☐ Pending ☐ Submitted ☐ Accepted
Control System Password Handoff to Owner |  |  |  |  | ☐ Pending ☐ Submitted ☐ Accepted
BAS Remote Access Setup & Tested |  |  |  |  | ☐ Pending ☐ Submitted ☐ Accepted
Training Sign-Off Sheets (all sessions) |  |  |  |  | ☐ Pending ☐ Submitted ☐ Accepted
LEED Cx Documentation Package (if applicable) |  |  |  |  | ☐ Pending ☐ Submitted ☐ Accepted
Certificate of Substantial Completion (Cx portion) |  |  |  |  | ☐ Pending ☐ Submitted ☐ Accepted
✍️ SECTION D — FINAL PROJECT CLOSEOUT & CERTIFICATION
Commissioning Authority (CxA):
CxA Signature / Date:
Mechanical Contractor:
Contractor Signature / Date:
Electrical Contractor:
Contractor Signature / Date:
Controls Contractor:
Contractor Signature / Date:
Engineer of Record (EOR):
EOR Signature / Date:
Owner Representative:
Owner Signature / Date:
Project Commissioning Status: |  |  | ☐ Commissioning Complete ☐ Conditional Acceptance ☐ Ongoing — Seasonal / Deferred Cx
Your HVAC Co. • Rogers, AR • (555) 867-5309 • www.yourhvac.com • EPA 608 Universal • NATE Certified