## QA Plan & Project Scope
Your HVAC Co. |  |  |  | HVAC QA/QC CHECKLIST TEMPLATE
Rogers, AR • (555) 867-5309 • www.yourhvac.com • service@yourhvac.com
📋 SECTION 1 — PROJECT IDENTIFICATION & QA TEAM
Project Name / Description:
Project Number / Job #:
Project Address:
City / State / ZIP:
Building Owner / Client:
Owner QA Representative:
General Contractor:
GC QA Contact & Phone:
Mechanical Contractor:
Mech. QA Contact & Phone:
Sheet Metal / Duct Contractor:
Sheet Metal QA Contact & Phone:
Insulation Contractor:
Insulation QA Contact & Phone:
Controls / BAS Contractor:
Controls QA Contact & Phone:
HVAC Inspector / AHJ Contact:
Inspection Agency (3rd party):
Project Engineer of Record (EOR):
EOR QA Contact & Phone:
Applicable Codes (IMC / SMC / IBC / ASHRAE):
Project Start Date:
Mechanical Rough-In Complete Date:
Inspection Milestone Dates:
Mechanical Completion Date:
📐 SECTION 2 — QA/QC PLAN SUMMARY & INSPECTION HOLD POINTS
⬟ HOLD POINT LEGEND: Rows marked ⬟ in amber are MANDATORY HOLD POINTS — work may NOT proceed past this point until the inspector signs off. All other rows are standard QC verification points requiring documentation but not a formal hold. REJECT = nonconformance report (NCR) required.
⬟ SECTION 3 — MANDATORY HOLD POINT REGISTER
Hold Point # | Phase / Activity | Hold Point Description | Responsible Party | Inspector / Witness | Scheduled Date | Sign-Off Date / Status
HP-01 | Rough-In | Ductwork layout verified against drawings before concealment | Mech. Contractor | Inspector / EOR |  | ☐ Approved ☐ Conditional ☐ Rejected
HP-02 | Rough-In | Equipment curb/structural support inspected before unit set | Mech. Contractor | Inspector / GC |  | ☐ Approved ☐ Conditional ☐ Rejected
HP-03 | Rough-In | Refrigerant piping pressure test (nitrogen) witnessed before insulation | Mech. Contractor | Inspector / EOR |  | ☐ Approved ☐ Conditional ☐ Rejected
HP-04 | Rough-In | Ductwork leakage test (duct blaster) witnessed before concealment | Duct Contractor | Inspector / EOR |  | ☐ Approved ☐ Conditional ☐ Rejected
HP-05 | Rough-In | Hydronic piping pressure test witnessed before concealment | Mech. Contractor | Inspector |  | ☐ Approved ☐ Conditional ☐ Rejected
HP-06 | Rough-In | Underground piping inspection before backfill (geothermal / CHW) | Mech. Contractor | Inspector / AHJ |  | ☐ Approved ☐ Conditional ☐ Rejected
HP-07 | Insulation | Pipe and duct insulation inspection before above-ceiling close-in | Insulation Cont. | Inspector |  | ☐ Approved ☐ Conditional ☐ Rejected
HP-08 | Equipment Set | Equipment installation verified before electrical connection | Mech. Contractor | Inspector / EOR |  | ☐ Approved ☐ Conditional ☐ Rejected
HP-09 | Controls | Controls point-to-point checkout complete before startup | Controls Cont. | CxA / Inspector |  | ☐ Approved ☐ Conditional ☐ Rejected
HP-10 | Pre-Startup | Prefunctional Checklist (PFC) signed before first energization | Mech. Contractor | CxA / Inspector |  | ☐ Approved ☐ Conditional ☐ Rejected
HP-11 | Startup | Test & Balance (TAB) complete before owner occupancy | TAB Agent | EOR / Owner |  | ☐ Approved ☐ Conditional ☐ Rejected
HP-12 | Closeout | All NCRs resolved before final inspection | Mech. Contractor | Inspector / Owner |  | ☐ Approved ☐ Conditional ☐ Rejected
📝 SECTION 4 — NONCONFORMANCE REPORT (NCR) LOG
NCR # | Date Issued | Location / Unit | Nonconformance Description | Issued By | Responsible Party | Resolution / Closure Date
NCR-01 | [5 empty] | ☐ Open ☐ In Review ☐ Closed
NCR-02 | [5 empty] | ☐ Open ☐ In Review ☐ Closed
NCR-03 | [5 empty] | ☐ Open ☐ In Review ☐ Closed
NCR-04 | [5 empty] | ☐ Open ☐ In Review ☐ Closed
NCR-05 | [5 empty] | ☐ Open ☐ In Review ☐ Closed
NCR-06 | [5 empty] | ☐ Open ☐ In Review ☐ Closed
NCR-07 | [5 empty] | ☐ Open ☐ In Review ☐ Closed
NCR-08 | [5 empty] | ☐ Open ☐ In Review ☐ Closed
NCR-09 | [5 empty] | ☐ Open ☐ In Review ☐ Closed
NCR-10 | [5 empty] | ☐ Open ☐ In Review ☐ Closed
NCR-11 | [5 empty] | ☐ Open ☐ In Review ☐ Closed
NCR-12 | [5 empty] | ☐ Open ☐ In Review ☐ Closed
NCR-13 | [5 empty] | ☐ Open ☐ In Review ☐ Closed
NCR-14 | [5 empty] | ☐ Open ☐ In Review ☐ Closed
NCR-15 | [5 empty] | ☐ Open ☐ In Review ☐ Closed
NCR-16 | [5 empty] | ☐ Open ☐ In Review ☐ Closed
NCR-17 | [5 empty] | ☐ Open ☐ In Review ☐ Closed
NCR-18 | [5 empty] | ☐ Open ☐ In Review ☐ Closed
NCR-19 | [5 empty] | ☐ Open ☐ In Review ☐ Closed
NCR-20 | [5 empty] | ☐ Open ☐ In Review ☐ Closed
NCR-21 | [5 empty] | ☐ Open ☐ In Review ☐ Closed
NCR-22 | [5 empty] | ☐ Open ☐ In Review ☐ Closed
NCR-23 | [5 empty] | ☐ Open ☐ In Review ☐ Closed
NCR-24 | [5 empty] | ☐ Open ☐ In Review ☐ Closed
NCR-25 | [5 empty] | ☐ Open ☐ In Review ☐ Closed
Your HVAC Co. • Rogers, AR • (555) 867-5309 • www.yourhvac.com • EPA 608 Universal • NATE Certified

## Equipment & Material Receiving
Your HVAC Co. |  |  |  | EQUIPMENT & MATERIAL RECEIVING QC
Rogers, AR • (555) 867-5309 • www.yourhvac.com • service@yourhvac.com
📦 SECTION 5 — EQUIPMENT RECEIVING INSPECTION
▸ General Receiving — All Major Equipment
# | QA/QC Inspection Point | Accept | Reject | N/A | Inspector Measurement / Finding | Corrective Action / Notes
1 | Purchase order and submittal approved before equipment was released for shipment | ☐ | ☐ | ☐
2 | Equipment model and serial number matches approved submittal and PO exactly | ☐ | ☐ | ☐
3 | Refrigerant type on nameplate matches specification and design drawings | ☐ | ☐ | ☐
4 | Electrical characteristics (voltage, phase, Hz, MCA, MOCP) match project drawings | ☐ | ☐ | ☐
5 | Equipment arrived undamaged — all six sides of packaging inspected | ☐ | ☐ | ☐
6 | Forklift / rigging damage check: base rails, refrigerant piping, condenser coil fins | ☐ | ☐ | ☐
7 | All factory-installed accessories present: TXV, economizer, filters, controls, remote panels | ☐ | ☐ | ☐
8 | Manufacturer's startup and commissioning requirements reviewed and on file | ☐ | ☐ | ☐
9 | O&M manuals, wiring diagrams, and parts list received and filed | ☐ | ☐ | ☐
10 | Warranty documentation received, dated, and on file | ☐ | ☐ | ☐
11 | Equipment serial numbers photographed and logged in equipment register | ☐ | ☐ | ☐
12 | Shipping damage claim filed within carrier's required window (if damage found) | ☐ | ☐ | ☐
▸ Rooftop Units (RTU) & Packaged Equipment
# | QA/QC Inspection Point | Accept | Reject | N/A | Inspector Measurement / Finding | Corrective Action / Notes
1 | Condenser coil fins inspected — less than 10% fin damage acceptable at delivery | ☐ | ☐ | ☐
2 | Fan blades inspected — no cracks, bends, or shipping damage | ☐ | ☐ | ☐
3 | Compressor(s) shipping blocks / restraints present (to be removed at startup only) | ☐ | ☐ | ☐
4 | Crankcase heater wiring confirmed intact | ☐ | ☐ | ☐
5 | Economizer assembly (if factory-installed) present and undamaged | ☐ | ☐ | ☐
6 | Gas orifice and manifold assembly intact (gas units) | ☐ | ☐ | ☐
7 | Control board and wiring harness verified undamaged | ☐ | ☐ | ☐
8 | Unit curb dimensions verified match rooftop curb on site | ☐ | ☐ | ☐
▸ Air Handling Units (AHU) — Field-Erected & Factory-Assembled
# | QA/QC Inspection Point | Accept | Reject | N/A | Inspector Measurement / Finding | Corrective Action / Notes
1 | AHU sections match submittal drawings — correct sequence and configuration | ☐ | ☐ | ☐
2 | Coil connections (supply and return) match design drawings — location and size | ☐ | ☐ | ☐
3 | Drain pan depth, slope, and connection size per specification | ☐ | ☐ | ☐
4 | Access doors on correct sections per maintenance requirements and contract documents | ☐ | ☐ | ☐
5 | Coil fins undamaged — straightening required if >10% of face area impacted | ☐ | ☐ | ☐
6 | Fan assembly ships separate — shaft, bearings, and drive received | ☐ | ☐ | ☐
7 | Motor horsepower, voltage, and efficiency match submittal | ☐ | ☐ | ☐
8 | VFD (if specified) received, model matches submittal, and shipped separately from AHU | ☐ | ☐ | ☐
▸ Chillers, Cooling Towers & Condensing Units
# | QA/QC Inspection Point | Accept | Reject | N/A | Inspector Measurement / Finding | Corrective Action / Notes
1 | Chiller shipped with nitrogen holding charge — pressure verified at receiving (5–10 psig) | ☐ | ☐ | ☐
2 | Chiller tubes inspected for shipping damage — end caps intact | ☐ | ☐ | ☐
3 | Cooling tower fill media received, packaged, and undamaged | ☐ | ☐ | ☐
4 | Condenser fan blades and hub assemblies undamaged | ☐ | ☐ | ☐
5 | Refrigerant charge status documented (factory-charged or field-charged) | ☐ | ☐ | ☐
6 | Variable speed drive (VFD) for compressor received and verified against submittal | ☐ | ☐ | ☐
7 | Chiller controls panel and remote monitoring hardware received | ☐ | ☐ | ☐
🔩 SECTION 6 — MATERIAL & COMPONENT RECEIVING QC
▸ Ductwork & Sheet Metal
# | QA/QC Inspection Point | Accept | Reject | N/A | Inspector Measurement / Finding | Corrective Action / Notes
1 | Duct gauge matches specification for each pressure class (e.g., 16 ga. for 4 in. w.c.) | ☐ | ☐ | ☐
2 | SMACNA construction class verified — seam type and reinforcement match pressure class | ☐ | ☐ | ☐
3 | Duct liner (if specified) correct density and thickness (1.5 lb/ft³ min. typical) | ☐ | ☐ | ☐
4 | Duct wrap (if specified) correct R-value, vapor barrier facing correct | ☐ | ☐ | ☐
5 | Flexible duct: UL 181 listed, correct internal diameter, correct R-value jacket | ☐ | ☐ | ☐
6 | Fire dampers: UL listed, correct UL classification (1½ hr or 3 hr), correct size | ☐ | ☐ | ☐
7 | Smoke dampers: UL listed, correct leakage class, correct actuator voltage | ☐ | ☐ | ☐
8 | VAV boxes: model, size, and controls options match approved submittal | ☐ | ☐ | ☐
9 | Diffusers, registers, and grilles: match submittal schedule (neck size, pattern, finish) | ☐ | ☐ | ☐
▸ Piping, Valves & Fittings
# | QA/QC Inspection Point | Accept | Reject | N/A | Inspector Measurement / Finding | Corrective Action / Notes
1 | Refrigerant copper tubing: ACR-rated, Type L or K per specification, clean/capped | ☐ | ☐ | ☐
2 | Refrigerant line set insulation: correct thickness and closed-cell type per spec | ☐ | ☐ | ☐
3 | Hydronic pipe: schedule and material match specification (Sch. 40, Sch. 80, Type L copper) | ☐ | ☐ | ☐
4 | Hydronic fittings: correct material and pressure rating for system design pressure | ☐ | ☐ | ☐
5 | Isolation valves: correct type (ball / butterfly / gate), pressure rating, and end connection | ☐ | ☐ | ☐
6 | Balancing valves: correct model, size, and Cv per hydronic schedule | ☐ | ☐ | ☐
7 | Strainers: correct mesh size and blow-down connection per specification | ☐ | ☐ | ☐
8 | Flexible pipe connectors / vibration isolators: correct pressure rating and size | ☐ | ☐ | ☐
9 | Chemical treatment equipment and chemicals received (glycol, inhibitor, biocide) | ☐ | ☐ | ☐
10 | Pressure relief valves: correct set pressure and capacity per ASME requirements | ☐ | ☐ | ☐
▸ Controls, Sensors & Electrical
# | QA/QC Inspection Point | Accept | Reject | N/A | Inspector Measurement / Finding | Corrective Action / Notes
1 | BAS/DDC controllers: model and I/O count match approved submittal and point list | ☐ | ☐ | ☐
2 | Temperature sensors: correct type (RTD / thermistor / 4-20mA), range, and accuracy | ☐ | ☐ | ☐
3 | Humidity sensors: correct range (%RH), accuracy, and output signal | ☐ | ☐ | ☐
4 | CO2 sensors: dual-beam NDIR type, correct range (0–2000 ppm), factory-calibrated | ☐ | ☐ | ☐
5 | Airflow stations / flow measuring stations: correct duct size and calibrated | ☐ | ☐ | ☐
6 | Actuators (damper / valve): correct torque, spring return, and voltage per controls spec | ☐ | ☐ | ☐
7 | Thermostats / zone controllers: correct model, features (humidity, CO2, occupancy) per spec | ☐ | ☐ | ☐
8 | VFDs: correct HP, voltage, bypass option, and I/O per motor schedule | ☐ | ☐ | ☐
9 | Control panel enclosures: correct NEMA rating for location (NEMA 1 / NEMA 4 / NEMA 12) | ☐ | ☐ | ☐
10 | Wire and cable: correct gauge, insulation type, and shielding per controls spec | ☐ | ☐ | ☐
Your HVAC Co. • Rogers, AR • (555) 867-5309 • www.yourhvac.com • EPA 608 Universal • NATE Certified

## Installation QC Inspections
Your HVAC Co. |  |  |  | INSTALLATION QC INSPECTIONS
Rogers, AR • (555) 867-5309 • www.yourhvac.com • service@yourhvac.com
🏗️ SECTION 7 — EQUIPMENT INSTALLATION QC
▸ Equipment Placement & Structural
# | QA/QC Inspection Point | Accept | Reject | N/A | Inspector Measurement / Finding | Corrective Action / Notes
1 | Equipment location matches mechanical drawings — within 2 in. tolerance | ☐ | ☐ | ☐
⬟ | HOLD: Roof curb installed level (±1/8 in. over 48 in.) and flashed watertight — HOLD | ☐ | ☐ | ☐
3 | Curb dimensions match unit base frame — no overhang or gap greater than 1/2 in. | ☐ | ☐ | ☐
4 | Unit set on curb — shipping feet removed, unit sits flush and level | ☐ | ☐ | ☐
5 | Vibration isolators installed per manufacturer and specification | ☐ | ☐ | ☐
6 | Service clearances confirmed on all sides per manufacturer minimums | ☐ | ☐ | ☐
7 | Rigging attachment points used correctly — no field-welded lugs or unapproved lifts | ☐ | ☐ | ☐
⬟ | HOLD: Rooftop unit weight vs. structural support capacity confirmed with EOR | ☐ | ☐ | ☐
9 | Equipment nameplates photographed and logged in equipment register | ☐ | ☐ | ☐
10 | All shipping blocks, bolts, and temporary bracing removed | ☐ | ☐ | ☐
▸ Refrigerant Piping Installation
# | QA/QC Inspection Point | Accept | Reject | N/A | Inspector Measurement / Finding | Corrective Action / Notes
1 | Pipe sizing matches mechanical schedule — suction, discharge, and liquid lines | ☐ | ☐ | ☐
2 | Pipe route follows drawings — deviations approved in writing by EOR | ☐ | ☐ | ☐
3 | Suction line pitched toward compressor (1/2 in./10 ft. min.) where horizontal | ☐ | ☐ | ☐
4 | Vertical suction risers have oil traps at base and at every 20-ft. rise | ☐ | ☐ | ☐
5 | Liquid line is not exposed to direct heat sources or excessive sun without insulation | ☐ | ☐ | ☐
⬟ | HOLD: All brazed joints completed with nitrogen purge flowing (prevents copper oxidation) — HOLD | ☐ | ☐ | ☐
7 | Phosphorus-copper (Phos-Cu) brazing filler used for copper-to-copper (no flux required) | ☐ | ☐ | ☐
8 | Silver brazing alloy (45%) used for copper-to-brass or copper-to-steel joints (flux required) | ☐ | ☐ | ☐
9 | All joints visually inspected — no voids, pinholes, excessive oxidation, or drips | ☐ | ☐ | ☐
⬟ | HOLD: Leak test: nitrogen pressurized to 150 psig (or per mfr.) — 24-hr hold — HOLD | ☐ | ☐ | ☐
⬟ | HOLD: Leak check with electronic detector before insulation applied — no leaks found — HOLD | ☐ | ☐ | ☐
12 | Piping insulation applied: correct thickness, closed-cell, continuous vapor barrier | ☐ | ☐ | ☐
13 | Insulation joints sealed with vapor-barrier adhesive — no gaps or punctures | ☐ | ☐ | ☐
14 | Pipe hangers spaced per SMACNA / MSS SP-58 (copper: max 6 ft. for 1-in. and smaller) | ☐ | ☐ | ☐
15 | Hangers are isolated type (no metal-to-metal contact on insulated suction line) | ☐ | ☐ | ☐
16 | Service valves / access ports installed and accessible without removing insulation | ☐ | ☐ | ☐
17 | Filter/drier installed, oriented correctly (arrow toward compressor), and insulated | ☐ | ☐ | ☐
18 | Sight glass installed in liquid line, accessible and readable | ☐ | ☐ | ☐
▸ Hydronic Piping Installation
# | QA/QC Inspection Point | Accept | Reject | N/A | Inspector Measurement / Finding | Corrective Action / Notes
1 | Pipe slope maintained: minimum 1 in. per 40 ft. toward low-point drain | ☐ | ☐ | ☐
2 | Air vents installed at all system high points | ☐ | ☐ | ☐
3 | Low-point drain valves installed at all system low points | ☐ | ☐ | ☐
4 | Expansion tank installed at correct location — at system fill connection | ☐ | ☐ | ☐
5 | Pressure relief valve installed per ASME and piped to safe discharge | ☐ | ☐ | ☐
6 | Flow-balancing valves installed at all terminal units per hydronic schedule | ☐ | ☐ | ☐
7 | Strainers installed upstream of pumps and control valves — Y or basket type | ☐ | ☐ | ☐
8 | Isolation valves installed to allow equipment removal without system drain | ☐ | ☐ | ☐
9 | Pressure gauges installed at pump inlet and outlet, and coil connections | ☐ | ☐ | ☐
10 | Pressure/temperature (P/T) test ports installed per specification | ☐ | ☐ | ☐
11 | Flexible connectors installed at pump and equipment connections (vibration isolation) | ☐ | ☐ | ☐
⬟ | HOLD: System hydrostatically pressure-tested at 1.5× working pressure — 4-hr hold — HOLD | ☐ | ☐ | ☐
⬟ | HOLD: System flushed and cleaned per specification before equipment connection — HOLD | ☐ | ☐ | ☐
14 | Chemical treatment / glycol fill verified at correct concentration | ☐ | ☐ | ☐
💨 SECTION 8 — DUCTWORK INSTALLATION QC
▸ Sheet Metal Duct Construction
# | QA/QC Inspection Point | Accept | Reject | N/A | Inspector Measurement / Finding | Corrective Action / Notes
1 | Duct gauge verified at each pressure class — spot measurements taken and logged | ☐ | ☐ | ☐
2 | Duct seams: Pittsburgh lock (longitudinal) or snap-lock — correct for pressure class | ☐ | ☐ | ☐
3 | Transverse joints: S-slip and drive, TDC/TDF flange, or Ductmate — per SMACNA class | ☐ | ☐ | ☐
4 | Joint sealant: UL 181B-FX listed mastic or tape applied to all joints and seams | ☐ | ☐ | ☐
5 | Duct reinforcement / stiffeners installed per SMACNA Table — correct gauge and spacing | ☐ | ☐ | ☐
⬟ | HOLD: All rectangular duct joints sealed before concealment — HOLD for leakage test | ☐ | ☐ | ☐
⬟ | HOLD: Duct leakage test performed: max 4% leakage for Seal Class A (or per spec) — HOLD | ☐ | ☐ | ☐
8 | Round spiral duct: correct gauge, UL 181 listed, slip joints sealed with mastic | ☐ | ☐ | ☐
9 | Flexible duct: no kinks, fully extended (max 1 compression ratio), max 4-ft. sections | ☐ | ☐ | ☐
10 | Flexible duct connections to collar: 2 layers of listed tape + draw band | ☐ | ☐ | ☐
11 | Supply diffuser necks connected to ductwork with mastic seal — no foil tape only | ☐ | ☐ | ☐
12 | Return air pathways open and unobstructed — no partition blockage | ☐ | ☐ | ☐
13 | Exhaust / toilet exhaust duct terminates outdoors — not in attic or interstitial space | ☐ | ☐ | ☐
14 | Kitchen exhaust duct: Type 1 stainless or black iron, all welded — per IMC Chapter 5 | ☐ | ☐ | ☐
▸ Duct Insulation & Vapor Barrier
# | QA/QC Inspection Point | Accept | Reject | N/A | Inspector Measurement / Finding | Corrective Action / Notes
1 | Duct insulation type and R-value matches specification (R-6 supply, R-4.2 return typical) | ☐ | ☐ | ☐
2 | Insulation applied to all sheet metal supply and return ductwork in unconditioned spaces | ☐ | ☐ | ☐
3 | Insulation continuity maintained at all hangers — no compression greater than 1/3 thickness | ☐ | ☐ | ☐
4 | Vapor barrier intact and continuous on all exterior duct insulation — no punctures | ☐ | ☐ | ☐
5 | Duct liner (internal) applied smooth-side to airstream — no exposed raw fiberglass | ☐ | ☐ | ☐
6 | Duct liner joints and seams sealed with liner adhesive — no gaps or delamination | ☐ | ☐ | ☐
7 | Insulation terminated neatly at diffuser necks and VAV box inlets — no raw edges exposed | ☐ | ☐ | ☐
▸ Dampers, Fire / Smoke Dampers & Access
# | QA/QC Inspection Point | Accept | Reject | N/A | Inspector Measurement / Finding | Corrective Action / Notes
1 | Fire dampers installed at all rated wall and floor penetrations per drawings | ☐ | ☐ | ☐
2 | Fire dampers accessible for reset — listed access door installed within 18 in. of damper | ☐ | ☐ | ☐
3 | Fire damper sleeves: correct gauge (16 ga. min.) and clearance for thermal expansion | ☐ | ☐ | ☐
4 | Smoke dampers installed per drawing and specification — correct leakage class | ☐ | ☐ | ☐
5 | Smoke damper end switches wired and reporting to BAS / fire alarm panel | ☐ | ☐ | ☐
6 | Volume dampers installed at each branch takeoff — accessible and labeled | ☐ | ☐ | ☐
7 | Outdoor air intake damper blades and seals intact — full close verified before startup | ☐ | ☐ | ☐
8 | Exhaust air damper blades and seals intact — no rattling or misalignment | ☐ | ☐ | ☐
9 | Access doors installed in ductwork at all coils, dampers, and fire dampers — per spec | ☐ | ☐ | ☐
⚡ SECTION 9 — ELECTRICAL INSTALLATION QC
# | QA/QC Inspection Point | Accept | Reject | N/A | Inspector Measurement / Finding | Corrective Action / Notes
1 | Electrical disconnect installed within line of sight of unit — per NEC 440.14 | ☐ | ☐ | ☐
2 | Disconnect ampacity and voltage rating match unit MCA / MOCP on nameplate | ☐ | ☐ | ☐
3 | Wire gauge sized per NEC for MCA — no undersized conductors | ☐ | ☐ | ☐
4 | Overcurrent protection (fuse / breaker) at or below MOCP on nameplate | ☐ | ☐ | ☐
5 | Equipment grounding conductor installed and bonded — correct gauge per NEC 250 | ☐ | ☐ | ☐
6 | All terminations torqued to manufacturer specification — lug torque values documented | ☐ | ☐ | ☐
7 | High-voltage conductors separated from low-voltage control wiring by 2 in. min. | ☐ | ☐ | ☐
8 | Conduit support spacing per NEC — no unsupported spans greater than 10 ft. | ☐ | ☐ | ☐
9 | Conduit bodies, junction boxes, and pull boxes accessible and covers installed | ☐ | ☐ | ☐
10 | Low-voltage wiring: shielded cable used for analog signals — shield grounded at one end only | ☐ | ☐ | ☐
11 | Wire labels installed at both ends of every conductor — match as-built drawings | ☐ | ☐ | ☐
12 | Electrical panel circuit labeling complete and accurate — no unlabeled breakers | ☐ | ☐ | ☐
13 | Crankcase heater energized minimum 24 hours before compressor startup | ☐ | ☐ | ☐
14 | VFD programmed per submittal — output frequency, accel/decel ramp, fault settings | ☐ | ☐ | ☐
15 | VFD bypass mode tested — unit runs on bypass contactor if VFD faults | ☐ | ☐ | ☐
🖥️ SECTION 10 — CONTROLS & BAS INSTALLATION QC
# | QA/QC Inspection Point | Accept | Reject | N/A | Inspector Measurement / Finding | Corrective Action / Notes
1 | BAS controller installation location matches submittal — accessible and ventilated | ☐ | ☐ | ☐
2 | Point-to-point checkout complete for all analog inputs — signal verified at controller | ☐ | ☐ | ☐
3 | Point-to-point checkout complete for all analog outputs — actuator responds to command | ☐ | ☐ | ☐
4 | Point-to-point checkout complete for all digital inputs — correct ON/OFF state shown in BAS | ☐ | ☐ | ☐
5 | Point-to-point checkout complete for all digital outputs — correct relay operation | ☐ | ☐ | ☐
6 | All sensors installed at correct locations — no sensors in dead legs or stratified zones | ☐ | ☐ | ☐
7 | Temperature sensor well installation: immersion depth, thermal compound applied | ☐ | ☐ | ☐
8 | Duct static pressure sensors: correct location (2/3 down longest duct run) | ☐ | ☐ | ☐
9 | Room CO2 sensors: 5 ft. above floor, in return air path — not above diffuser | ☐ | ☐ | ☐
10 | Actuators wired and phased correctly — damper opens on increasing signal | ☐ | ☐ | ☐
⬟ | HOLD: Sequence of operations programmed and field-verified against approved SOO | ☐ | ☐ | ☐
12 | All control panels labeled — circuit numbers, point descriptions, controller ID | ☐ | ☐ | ☐
13 | BAS communication network tested — all controllers online, no comm faults | ☐ | ☐ | ☐
⬟ | HOLD: Smoke detector AHU interlock wired and tested — unit shuts down on alarm | ☐ | ☐ | ☐
⬟ | HOLD: Emergency stop wired and tested — unit de-energizes immediately | ☐ | ☐ | ☐
Your HVAC Co. • Rogers, AR • (555) 867-5309 • www.yourhvac.com • EPA 608 Universal • NATE Certified

## Workmanship & Code Compliance
Your HVAC Co. |  |  |  | WORKMANSHIP STANDARDS & CODE COMPLIANCE QC
Rogers, AR • (555) 867-5309 • www.yourhvac.com • service@yourhvac.com
📏 SECTION 11 — WORKMANSHIP STANDARDS VERIFICATION
▸ General Workmanship
# | QA/QC Inspection Point | Accept | Reject | N/A | Inspector Measurement / Finding | Corrective Action / Notes
1 | All work performed by qualified journeyman mechanics or licensed technicians | ☐ | ☐ | ☐
2 | Work area kept clean — no debris left in air handlers, ducts, or equipment pads | ☐ | ☐ | ☐
3 | No unauthorized field modifications to equipment without written EOR approval | ☐ | ☐ | ☐
4 | All penetrations through fire-rated walls/floors sealed with listed firestop system | ☐ | ☐ | ☐
5 | Roof and wall penetrations waterproofed — no open or unsealed penetrations | ☐ | ☐ | ☐
6 | All equipment, piping, and ductwork labeled per specification (minimum 25-ft. spacing) | ☐ | ☐ | ☐
7 | Pipe and duct identification includes flow direction arrows | ☐ | ☐ | ☐
8 | Zone/area labels on all supply diffusers and return grilles match TAB drawings | ☐ | ☐ | ☐
9 | No cross-threading, stripped fasteners, or over-torqued fittings present | ☐ | ☐ | ☐
10 | Tools and consumables (rags, wire nuts, tape scraps) removed from all unit interiors | ☐ | ☐ | ☐
11 | All temporary protective covers removed from equipment before startup | ☐ | ☐ | ☐
12 | Final worksite broom-swept and construction debris hauled off before inspection | ☐ | ☐ | ☐
▸ Hanger & Support Standards
# | QA/QC Inspection Point | Accept | Reject | N/A | Inspector Measurement / Finding | Corrective Action / Notes
1 | All duct hangers: trapeze style with all-thread rod — no wire or strap hangers on rigid duct | ☐ | ☐ | ☐
2 | Hanger spacing for rectangular duct: max 8 ft. longitudinal (per SMACNA Table 4-1) | ☐ | ☐ | ☐
3 | Hanger spacing for round duct: max 10 ft. per SMACNA | ☐ | ☐ | ☐
4 | All-thread rod diameter: 3/8 in. min. for duct up to 60 in., 1/2 in. for larger | ☐ | ☐ | ☐
5 | Pipe hangers sized per MSS SP-58 and spaced per SMACNA/ASHRAE for pipe size | ☐ | ☐ | ☐
6 | Hanger inserts in concrete poured correctly — no hilti anchors into topping slabs | ☐ | ☐ | ☐
7 | No ductwork, piping, or conduit resting on ceiling grid or other unrated support | ☐ | ☐ | ☐
8 | Seismic bracing installed per IBC Chapter 13 and SMACNA seismic requirements | ☐ | ☐ | ☐
9 | Equipment anchored to structure per seismic requirements — anchor bolt sizes documented | ☐ | ☐ | ☐
📖 SECTION 12 — CODE COMPLIANCE VERIFICATION
▸ International Mechanical Code (IMC) Compliance
# | QA/QC Inspection Point | Accept | Reject | N/A | Inspector Measurement / Finding | Corrective Action / Notes
1 | Equipment clearances per IMC Section 306 — working space and access maintained | ☐ | ☐ | ☐
2 | Combustion air provisions per IMC Chapter 7 (gas-fired equipment in mechanical rooms) | ☐ | ☐ | ☐
3 | Ventilation rates comply with ASHRAE 62.1 — OA CFM verified per occupancy type | ☐ | ☐ | ☐
4 | Exhaust system routing per IMC Chapter 5 — correct termination location and clearances | ☐ | ☐ | ☐
5 | Clothes dryer exhaust (if applicable): smooth-bore metal duct, max 25-ft. equivalent length | ☐ | ☐ | ☐
6 | Mechanical room height and area per IMC Section 1101 (refrigerant equipment) | ☐ | ☐ | ☐
7 | Refrigerant quantity per area verified — no exceed per IMC Table 1103.1 for occupancy type | ☐ | ☐ | ☐
8 | Emergency pressure relief vent piped to outdoors per ASHRAE 15 (large refrigerant systems) | ☐ | ☐ | ☐
9 | Equipment shut-off interlock with fire alarm per IMC / local amendments | ☐ | ☐ | ☐
10 | Gas piping tested per IMC Section 1312 — pressure test documentation on file | ☐ | ☐ | ☐
▸ Energy Code Compliance (ASHRAE 90.1 / IECC)
# | QA/QC Inspection Point | Accept | Reject | N/A | Inspector Measurement / Finding | Corrective Action / Notes
1 | Equipment efficiency meets or exceeds ASHRAE 90.1 minimum (EER, COP, IEER, SEER2) | ☐ | ☐ | ☐
2 | Economizer provided on systems required per ASHRAE 90.1 Table 6.5.1 | ☐ | ☐ | ☐
3 | Duct insulation R-values meet ASHRAE 90.1 Table 6.8.2 minimums | ☐ | ☐ | ☐
4 | Pipe insulation R-values meet ASHRAE 90.1 Table 6.8.3 minimums | ☐ | ☐ | ☐
5 | Demand-controlled ventilation (DCV) installed where required per 90.1 Section 6.4.3.8 | ☐ | ☐ | ☐
6 | Exhaust air energy recovery installed where required per 90.1 Section 6.5.6 | ☐ | ☐ | ☐
7 | Zone controls: each zone has individual thermostat or sensor — no multi-zone single-point control | ☐ | ☐ | ☐
8 | Supply air temperature reset controls programmed per 90.1 Section 6.5.3.3 (if applicable) | ☐ | ☐ | ☐
9 | Motor efficiencies meet NEMA Premium or ASHRAE 90.1 minimums | ☐ | ☐ | ☐
10 | Fan system brake horsepower (BHP) does not exceed ASHRAE 90.1 Table 6.5.3.1 limits | ☐ | ☐ | ☐
11 | Building envelope air sealing: mechanical penetrations sealed per energy code | ☐ | ☐ | ☐
▸ Indoor Air Quality & Refrigerant (ASHRAE 15 / 62.1)
# | QA/QC Inspection Point | Accept | Reject | N/A | Inspector Measurement / Finding | Corrective Action / Notes
1 | Refrigerant type is not phased out or restricted under AIM Act / EPA SNAP regulations | ☐ | ☐ | ☐
2 | Refrigerant room sensor installed per ASHRAE 15 (if system charge exceeds threshold) | ☐ | ☐ | ☐
3 | Emergency ventilation (exhaust) interlocked with refrigerant detector per ASHRAE 15 | ☐ | ☐ | ☐
4 | Refrigerant piping in occupied space protected (casing, shafts, or concealed routing) | ☐ | ☐ | ☐
5 | Makeup air unit (MAU) or DOAS sized for minimum OA per ASHRAE 62.1 Ventilation Table | ☐ | ☐ | ☐
6 | Dedicated outdoor air system (DOAS) delivers 100% OA to all zones served | ☐ | ☐ | ☐
7 | Air filtration minimum MERV-8 on all recirculated air per ASHRAE 62.1 Section 6.4.5 | ☐ | ☐ | ☐
8 | Exhaust terminals located per ASHRAE 62.1 Table 6-4 clearances from intakes | ☐ | ☐ | ☐
9 | Plumbing code compliance: trap primers on floor drains in mechanical rooms | ☐ | ☐ | ☐
▸ AHJ Permit & Inspection Compliance
# | QA/QC Inspection Point | Accept | Reject | N/A | Inspector Measurement / Finding | Corrective Action / Notes
1 | Mechanical permit obtained and posted at job site before work commenced | ☐ | ☐ | ☐
2 | Approved permit drawings available on site — current approved set used in field | ☐ | ☐ | ☐
3 | All required AHJ inspections scheduled and passed: rough-in, gas, final | ☐ | ☐ | ☐
4 | AHJ inspection correction notices addressed and re-inspection completed | ☐ | ☐ | ☐
5 | Certificate of occupancy (CO) or AHJ final sign-off received before turnover | ☐ | ☐ | ☐
6 | Pressure vessel registration (boilers / large pressure vessels) on file with state | ☐ | ☐ | ☐
7 | Gas piping final test witnessed by AHJ inspector | ☐ | ☐ | ☐
8 | All deferred submittals approved by building department before work performed | ☐ | ☐ | ☐
Your HVAC Co. • Rogers, AR • (555) 867-5309 • www.yourhvac.com • EPA 608 Universal • NATE Certified

## QA Reports & Closeout
Your HVAC Co. |  |  |  | QA INSPECTION REPORTS & PROJECT CLOSEOUT
Rogers, AR • (555) 867-5309 • www.yourhvac.com • service@yourhvac.com
📊 SECTION 13 — QA INSPECTION REPORT LOG
Report # | Inspection Date | Phase / Area Inspected | Inspector Name | Items Inspected | NCRs Issued | Report Status
IR-01 | [5 empty] | ☐ Draft ☐ Issued ☐ Accepted ☐ Closed
IR-02 | [5 empty] | ☐ Draft ☐ Issued ☐ Accepted ☐ Closed
IR-03 | [5 empty] | ☐ Draft ☐ Issued ☐ Accepted ☐ Closed
IR-04 | [5 empty] | ☐ Draft ☐ Issued ☐ Accepted ☐ Closed
IR-05 | [5 empty] | ☐ Draft ☐ Issued ☐ Accepted ☐ Closed
IR-06 | [5 empty] | ☐ Draft ☐ Issued ☐ Accepted ☐ Closed
IR-07 | [5 empty] | ☐ Draft ☐ Issued ☐ Accepted ☐ Closed
IR-08 | [5 empty] | ☐ Draft ☐ Issued ☐ Accepted ☐ Closed
IR-09 | [5 empty] | ☐ Draft ☐ Issued ☐ Accepted ☐ Closed
IR-10 | [5 empty] | ☐ Draft ☐ Issued ☐ Accepted ☐ Closed
IR-11 | [5 empty] | ☐ Draft ☐ Issued ☐ Accepted ☐ Closed
IR-12 | [5 empty] | ☐ Draft ☐ Issued ☐ Accepted ☐ Closed
IR-13 | [5 empty] | ☐ Draft ☐ Issued ☐ Accepted ☐ Closed
IR-14 | [5 empty] | ☐ Draft ☐ Issued ☐ Accepted ☐ Closed
IR-15 | [5 empty] | ☐ Draft ☐ Issued ☐ Accepted ☐ Closed
IR-16 | [5 empty] | ☐ Draft ☐ Issued ☐ Accepted ☐ Closed
IR-17 | [5 empty] | ☐ Draft ☐ Issued ☐ Accepted ☐ Closed
IR-18 | [5 empty] | ☐ Draft ☐ Issued ☐ Accepted ☐ Closed
IR-19 | [5 empty] | ☐ Draft ☐ Issued ☐ Accepted ☐ Closed
IR-20 | [5 empty] | ☐ Draft ☐ Issued ☐ Accepted ☐ Closed
IR-21 | [5 empty] | ☐ Draft ☐ Issued ☐ Accepted ☐ Closed
IR-22 | [5 empty] | ☐ Draft ☐ Issued ☐ Accepted ☐ Closed
IR-23 | [5 empty] | ☐ Draft ☐ Issued ☐ Accepted ☐ Closed
IR-24 | [5 empty] | ☐ Draft ☐ Issued ☐ Accepted ☐ Closed
IR-25 | [5 empty] | ☐ Draft ☐ Issued ☐ Accepted ☐ Closed
IR-26 | [5 empty] | ☐ Draft ☐ Issued ☐ Accepted ☐ Closed
IR-27 | [5 empty] | ☐ Draft ☐ Issued ☐ Accepted ☐ Closed
IR-28 | [5 empty] | ☐ Draft ☐ Issued ☐ Accepted ☐ Closed
IR-29 | [5 empty] | ☐ Draft ☐ Issued ☐ Accepted ☐ Closed
IR-30 | [5 empty] | ☐ Draft ☐ Issued ☐ Accepted ☐ Closed
🔬 SECTION 14 — PRESSURE TEST & LEAK TEST RECORD
Test # | System / Area | Test Medium | Test Pressure (psig) | Test Duration | Witnessed By | Result / Date
PT-01 | Refrigerant Piping — System A | Dry Nitrogen | 150 psig (or per mfr.) | 24 hours |  | ☐ Pass ☐ Fail ☐ Pending
PT-02 | Refrigerant Piping — System B | Dry Nitrogen | 150 psig (or per mfr.) | 24 hours |  | ☐ Pass ☐ Fail ☐ Pending
PT-03 | Refrigerant Leak Check Post-Charge | Electronic Detector | Charged system | Full sweep |  | ☐ Pass ☐ Fail ☐ Pending
PT-04 | Hydronic Piping — Chilled Water | Water | 1.5× working pressure | 4 hours |  | ☐ Pass ☐ Fail ☐ Pending
PT-05 | Hydronic Piping — Hot Water | Water | 1.5× working pressure | 4 hours |  | ☐ Pass ☐ Fail ☐ Pending
PT-06 | Duct Leakage Test — Supply (Zone 1) | Air (duct blaster) | 1 in. w.c. | Per SMACNA |  | ☐ Pass ☐ Fail ☐ Pending
PT-07 | Duct Leakage Test — Supply (Zone 2) | Air (duct blaster) | 1 in. w.c. | Per SMACNA |  | ☐ Pass ☐ Fail ☐ Pending
PT-08 | Duct Leakage Test — Return | Air (duct blaster) | 1 in. w.c. | Per SMACNA |  | ☐ Pass ☐ Fail ☐ Pending
PT-09 | Gas Piping — Pressure Test | Air or Inert Gas | Per IMC Section 1312 | Per IMC |  | ☐ Pass ☐ Fail ☐ Pending
PT-10 | Condensate Piping — Flow Test | Water | Gravity flow | Visual check |  | ☐ Pass ☐ Fail ☐ Pending
PT-11 | Additional System (user-defined) |  |  |  |  | ☐ Pass ☐ Fail ☐ Pending
PT-12 | Additional System (user-defined) |  |  |  |  | ☐ Pass ☐ Fail ☐ Pending
✅ SECTION 15 — FINAL QA VERIFICATION BEFORE TURNOVER
# | QA/QC Inspection Point | Accept | Reject | N/A | Inspector Measurement / Finding | Corrective Action / Notes
⬟ | HOLD: All NCRs closed — no open nonconformances remain | ☐ | ☐ | ☐
⬟ | HOLD: All hold points signed off — HP register complete — HOLD | ☐ | ☐ | ☐
⬟ | HOLD: All AHJ inspections passed — permits finalized | ☐ | ☐ | ☐
4 | Duct leakage test results meet specification requirements | ☐ | ☐ | ☐
⬟ | HOLD: Refrigerant leak test results: zero leaks detected at turnover | ☐ | ☐ | ☐
6 | Hydronic system pressure tests passed and documented | ☐ | ☐ | ☐
⬟ | HOLD: Test & Balance (TAB) complete — all airflows and waterflows within ±10% of design | ☐ | ☐ | ☐
8 | Commissioning complete — all FPTs passed and documented | ☐ | ☐ | ☐
9 | All punch list items from QA inspections resolved | ☐ | ☐ | ☐
10 | Equipment labels and zone identification complete throughout facility | ☐ | ☐ | ☐
11 | All access doors, panels, and cleanouts operable and labeled | ☐ | ☐ | ☐
12 | As-built drawings reflect all field changes — EOR approved | ☐ | ☐ | ☐
13 | O&M manuals delivered and reviewed with owner facilities team | ☐ | ☐ | ☐
14 | Spare parts / attic stock delivered to owner — quantities verified | ☐ | ☐ | ☐
15 | Owner training on QA-sensitive systems complete (filters, coils, BAS) | ☐ | ☐ | ☐
16 | Final photo documentation package submitted to owner and EOR | ☐ | ☐ | ☐
⬟ | HOLD: QA/QC final report compiled and submitted — all signed checklists included | ☐ | ☐ | ☐
18 | Project QA/QC binder delivered to owner (digital + hard copy) | ☐ | ☐ | ☐
✍️ SECTION 16 — FINAL QA/QC PROJECT SIGN-OFF & CERTIFICATION
QA Inspector / 3rd Party Agency:
Inspector Signature / Date:
Mechanical Contractor QA Rep:
Contractor Signature / Date:
Sheet Metal Contractor QA Rep:
Contractor Signature / Date:
Controls Contractor QA Rep:
Contractor Signature / Date:
General Contractor:
GC Signature / Date:
Engineer of Record (EOR):
EOR Signature / Date:
Owner Representative:
Owner Signature / Date:
QA/QC Final Project Status: |  |  | ☐ QA Approved — Ready for Turnover ☐ Conditional Acceptance ☐ Not Approved — Outstanding Items
Your HVAC Co. • Rogers, AR • (555) 867-5309 • www.yourhvac.com • EPA 608 Universal • NATE Certified