## Start-Up Info & Equipment
Your HVAC Co. | HVAC EQUIPMENT START-UP REPORT
Rogers, AR • (555) 867-5309 • www.yourhvac.com • service@yourhvac.com
📋 SECTION 1 — PROJECT & JOB SITE INFORMATION
Project Name / Description:
Project Number / Job Number:
Project Address:
City / State / ZIP:
Building Owner / Client Name:
Owner Contact Name & Phone:
Owner Contact Email:
General Contractor:
GC Contact Name & Phone:
Mechanical Contractor:
Mechanical Contact Name & Phone:
Controls / BAS Contractor:
Controls Contact Name & Phone:
🏷️ SECTION 2 — EQUIPMENT NAMEPLATE & IDENTIFICATION
Unit Tag / Equipment ID:
Equipment Type / Category:
Manufacturer:
Model Number:
Serial Number:
Voltage / Phase / Hz:
MCA (Min. Circuit Ampacity):
MOCP (Max. Overcurrent Protection):
Refrigerant Type:
Factory Refrigerant Charge (lbs.):
Cooling Capacity (Btuh / Tons):
Heating Capacity (Btuh / kW):
Supply CFM (Design):
External Static Pressure (in. w.c.):
Installation Location / Zone:
Warranty Start Date:
👷 SECTION 3 — START-UP PERSONNEL & AUTHORIZATIONS
Lead Start-Up Technician:
Technician License / Cert #:
Assisting Technician (if applicable):
CxA / Commissioning Agent:
CxA Certification / License #:
Witnessed By (Owner / GC Rep):
Start-Up Date:
Start-Up Time (begin):
Start-Up Time (complete):
Ambient Temperature at Start-Up (°F):
Ambient Relative Humidity (%):
BAS / Controls Online? (Y/N):
TAB Completed Prior? (Y/N):
Crankcase Heater Energized 24 hrs? (Y/N):
© Your HVAC Co. ¦ Rogers, AR ¦ (555) 867-5309 ¦ www.yourhvac.com

## Pre-Start-Up Checklist
Your HVAC Co. |  |  |  | PRE-START-UP VERIFICATION CHECKLIST
Rogers, AR • (555) 867-5309 • www.yourhvac.com • service@yourhvac.com
🔍 PSU HEADER — COMPLETE BEFORE ENERGIZING UNIT
Unit Tag / Equipment ID:
Equipment Type:
Manufacturer / Model:
Serial Number:
Installation Location / Zone:
Technician Performing PSU Checklist:
Technician Name:
PSU Check Date:
Witnessed By (CxA / Owner Rep):
Witness Date:
🔩 PSU-A — MECHANICAL INSTALLATION VERIFICATION
# | Verification Point / Task | Pass | Fail | N/A | Measured / Observed | Tech Notes
1 | Unit installed per manufacturer's recommendations and project drawings | ☐ | ☐ | ☐
2 | Adequate service clearances maintained on all sides (per mfr. spec) | ☐ | ☐ | ☐
3 | Unit is level — verified with digital level (±0.5° tolerance) | ☐ | ☐ | ☐
4 | Vibration isolators / spring mounts installed and adjusted correctly | ☐ | ☐ | ☐
5 | Flexible duct connectors installed at unit supply and return connections | ☐ | ☐ | ☐
6 | All refrigerant piping connections made and visually inspected | ☐ | ☐ | ☐
7 | Refrigerant piping insulated and properly supported — no sags | ☐ | ☐ | ☐
8 | Condensate drain piping sloped correctly (1/8 in./ft. minimum) | ☐ | ☐ | ☐
9 | Condensate P-trap installed and properly sized per unit static pressure | ☐ | ☐ | ☐
10 | All ductwork connections secured — mastic or UL-181 tape applied | ☐ | ☐ | ☐
11 | Duct insulation properly installed — no gaps or compression | ☐ | ☐ | ☐
12 | Access panels present and operable — all screws in place | ☐ | ☐ | ☐
⚡ PSU-B — ELECTRICAL INSTALLATION VERIFICATION
# | Verification Point / Task | Pass | Fail | N/A | Measured / Observed | Tech Notes
1 | Disconnect switch installed and rated correctly per MCA / MOCP | ☐ | ☐ | ☐
2 | Wiring sized per NEC and manufacturer requirements (MCA verified) | ☐ | ☐ | ☐
3 | Overcurrent protection (breaker / fuse) ≤ MOCP rating on nameplate | ☐ | ☐ | ☐
4 | Ground conductor installed and properly terminated | ☐ | ☐ | ☐
5 | All electrical connections torqued to manufacturer specifications | ☐ | ☐ | ☐
6 | Unit voltage verified at disconnect — within ±10% of nameplate | ☐ | ☐ | ☐
7 | Phase rotation verified (3-phase units) — correct rotation confirmed | ☐ | ☐ | ☐
8 | Low-voltage control wiring installed per field wiring diagram | ☐ | ☐ | ☐
9 | Crankcase heater wired and confirmed energized for ≥ 24 hours | ☐ | ☐ | ☐
10 | Safety controls wired: high-pressure, low-pressure, freeze, smoke | ☐ | ☐ | ☐
11 | BAS / DDC points wired and controller online (if applicable) | ☐ | ☐ | ☐
12 | All junction boxes closed and covers in place | ☐ | ☐ | ☐
❄️ PSU-C — REFRIGERANT SYSTEM & CONTROLS PRE-CHECK
# | Verification Point / Task | Pass | Fail | N/A | Measured / Observed | Tech Notes
1 | Refrigerant type confirmed per nameplate — no substitutions | ☐ | ☐ | ☐
2 | System leak tested (nitrogen pressure test documented) | ☐ | ☐ | ☐
3 | System evacuated to ≤ 300 microns — decay test passed | ☐ | ☐ | ☐
4 | Factory charge verified OR field charge documented with scale weight | ☐ | ☐ | ☐
5 | Service valves open and Schrader cores installed | ☐ | ☐ | ☐
6 | Filter dryer installed — shipping caps removed | ☐ | ☐ | ☐
7 | Sight glass clear — no bubbles under operating conditions | ☐ | ☐ | ☐
8 | Thermostat / zone controller installed and set to correct setpoints | ☐ | ☐ | ☐
9 | Economizer controls verified (if applicable) | ☐ | ☐ | ☐
10 | Occupied / unoccupied schedules programmed | ☐ | ☐ | ☐
11 | Demand controlled ventilation (DCV) configured (if applicable) | ☐ | ☐ | ☐
© Your HVAC Co. ¦ Rogers, AR ¦ (555) 867-5309 ¦ www.yourhvac.com

## Startup Sequence & Tests
Your HVAC Co. |  |  |  | STARTUP SEQUENCE & OPERATIONAL TESTS
Rogers, AR • (555) 867-5309 • www.yourhvac.com • service@yourhvac.com
⚙️ TEST SESSION HEADER — COMPLETE AT EACH TEST SESSION
Unit Tag / Equipment ID:
Test Date:
Outdoor Air Temp at Test (°F):
Outdoor RH at Test (%):
Technician Name & Cert #:
Witness / CxA Name:
Previous PSU Checklist Approved? (Y/N):
Deficiencies Carried In From PSU:
🚀 ST-1 — INITIAL STARTUP SEQUENCE
# | Startup Task / Verification Point | Pass | Fail | N/A | Measured / Observed | Tech Notes
1 | All PSU items approved before energizing unit | ☐ | ☐ | ☐
2 | Energized unit at disconnect — no tripped breakers or fault codes | ☐ | ☐ | ☐
3 | Confirmed correct fan rotation — supply, return, condenser, exhaust | ☐ | ☐ | ☐
4 | No unusual vibration, noise, or mechanical interference on first start | ☐ | ☐ | ☐
5 | Unit completed first cooling cycle without fault or nuisance trip | ☐ | ☐ | ☐
6 | Unit completed first heating cycle without fault (gas/electric/HP) | ☐ | ☐ | ☐
7 | Defrost cycle tested (heat pump) — initiated and terminated correctly | ☐ | ☐ | ☐
8 | Emergency shut-down tested — unit de-energized immediately on E-stop | ☐ | ☐ | ☐
9 | All access panels closed and secured before extended operation | ☐ | ☐ | ☐
10 | Compressor staging verified (multi-stage / VFD units) | ☐ | ☐ | ☐
11 | Unit achieves design supply air temperature setpoint within 15 minutes | ☐ | ☐ | ☐
🛡️ ST-2 — SAFETY CONTROL VERIFICATION
# | Safety Control Verification | Pass | Fail | N/A | Trip Point / Set Point | Tech Notes
1 | High-pressure switch tested — compressor locks out at set point | ☐ | ☐ | ☐
2 | Low-pressure switch tested — compressor locks out at set point | ☐ | ☐ | ☐
3 | Freeze stat tested — fan / compressor lockout verified | ☐ | ☐ | ☐
4 | High-limit tested (gas heat) — burner lockout verified | ☐ | ☐ | ☐
5 | Smoke detector (supply/return) tested — unit shuts down on alarm | ☐ | ☐ | ☐
6 | Condensate overflow sensor tested — unit shuts down on water | ☐ | ☐ | ☐
7 | Phase-loss / phase-reversal protection tested (3-phase units) | ☐ | ☐ | ☐
8 | Low-ambient lockout tested (cooling) — unit locks out per set point | ☐ | ☐ | ☐
9 | Dirty-filter switch / IAQ interlock verified (if installed) | ☐ | ☐ | ☐
10 | Manual reset safety controls reset and documented | ☐ | ☐ | ☐
🖥️ ST-3 — CONTROLS & BAS INTEGRATION VERIFICATION
# | Controls Verification Point | Pass | Fail | N/A | Set Point / Value | Tech Notes
1 | Thermostat / DDC controller online — no fault codes | ☐ | ☐ | ☐
2 | All BAS points mapped and trending correctly | ☐ | ☐ | ☐
3 | Cooling setpoint command verified — unit responds correctly | ☐ | ☐ | ☐
4 | Heating setpoint command verified — unit responds correctly | ☐ | ☐ | ☐
5 | Fan-only mode verified — fan runs, compressor off | ☐ | ☐ | ☐
6 | Occupied / unoccupied modes verified — correct setback applied | ☐ | ☐ | ☐
7 | Economizer opens on command — OA damper verified at 100% open | ☐ | ☐ | ☐
8 | Economizer closes on high OA enthalpy / temp — verified | ☐ | ☐ | ☐
9 | DCV CO₂ control verified — OA damper modulates per CO₂ level | ☐ | ☐ | ☐
10 | Alarm points verified — BAS receives and annunciates unit faults | ☐ | ☐ | ☐
11 | BAS trend logs active — temps, pressures, runtime logged | ☐ | ☐ | ☐
© Your HVAC Co. ¦ Rogers, AR ¦ (555) 867-5309 ¦ www.yourhvac.com

## Measured Data & Performance
Your HVAC Co. |  |  |  | START-UP MEASURED DATA & PERFORMANCE VERIFICATION
Rogers, AR • (555) 867-5309 • www.yourhvac.com • service@yourhvac.com
⚡ SECTION A — ELECTRICAL MEASUREMENTS
Parameter | Nameplate / Spec | Measured Value | Unit | Tolerance | Status | Notes
Supply Voltage — L1 to L2 | Per nameplate ±10% |  | VAC | ±10% nameplate
Supply Voltage — L2 to L3 | Per nameplate ±10% |  | VAC | ±10% nameplate
Supply Voltage — L1 to L3 | Per nameplate ±10% |  | VAC | ±10% nameplate
Voltage Imbalance | ≤ 2% |  | % | ≤ 2%
Compressor Amps — L1 | ≤ nameplate RLA |  | Amps | ≤ RLA
Compressor Amps — L2 | ≤ nameplate RLA |  | Amps | ≤ RLA
Compressor Amps — L3 | ≤ nameplate RLA |  | Amps | ≤ RLA
Supply Fan Amps | ≤ nameplate FLA |  | Amps | ≤ FLA
Condenser Fan Amps (each) | ≤ nameplate FLA |  | Amps | ≤ FLA
Total Unit Amps (all loads) | ≤ MCA |  | Amps | ≤ MCA
🧊 SECTION B — REFRIGERANT SYSTEM MEASUREMENTS
Parameter | Design / Spec | Measured Value | Unit | Tolerance | Status | Notes
Refrigerant Type | Per nameplate |  | — | Exact match
Total Charge (lbs.) | Per nameplate |  | lbs. | Per mfr.
Suction Pressure | Varies by ref. |  | psig | Per chart
Discharge Pressure | Varies by ref. |  | psig | Per chart
Saturated Suction Temp | Varies by ref. |  | °F | Per chart
Saturated Discharge Temp | Varies by ref. |  | °F | Per chart
Evaporator Superheat | 8–12°F (TXV) |  | °F | ±2°F
Condenser Subcooling | 10–15°F |  | °F | ±2°F
Suction Line Temp (actual) | Per design |  | °F | ±3°F
Liquid Line Temp (actual) | Per design |  | °F | ±3°F
Compressor Discharge Temp | < 225°F typical |  | °F | < 225°F
Evaporator Coil Entering DB | Per design |  | °F | Per design
Evaporator Coil Leaving DB | Per design |  | °F | Per design
Evaporator Coil Delta-T | 16–22°F typical |  | °F | Per design
Condenser Entering Air Temp | Per design |  | °F | Per design
Condenser Leaving Air Temp | Per design |  | °F | Per design
💨 SECTION C — AIRSIDE PERFORMANCE VERIFICATION
Parameter | Design Value | Measured Value | Unit | % Deviation | Status | Notes
Total Supply CFM |  |  | CFM | ±10%
Total Return CFM |  |  | CFM | ±10%
Outdoor Air CFM (min.) |  |  | CFM | ±10%
Exhaust Air CFM |  |  | CFM | ±10%
Supply Static Pressure |  |  | in. w.c. | Per design
Return Static Pressure |  |  | in. w.c. | Per design
Total External Static Pressure |  |  | in. w.c. | ≤ unit ESP rating
Supply Air Temp — Cooling |  |  | °F | Per design
Supply Air Temp — Heating |  |  | °F | Per design
Return Air Temp — DB |  |  | °F | Per design
Return Air Temp — WB |  |  | °F | Per design
Mixed Air Temp (OA + RA) |  |  | °F | Calculated
Filter Pressure Drop (clean) |  |  | in. w.c. | Per mfr.
🔥 SECTION D — GAS / HEAT SYSTEM MEASUREMENTS (IF APPLICABLE)
Parameter | Design / Spec | Measured Value | Unit | Tolerance | Status | Notes
Gas Supply Pressure (at unit) | Per nameplate |  | in. w.c. | Per mfr.
Gas Manifold Pressure (operating) | Per nameplate |  | in. w.c. | Per mfr.
Flue Gas Temperature | Per design |  | °F | Per design
CO in Flue (undiluted) | < 400 ppm |  | ppm CO | < 400 ppm
Heat Exchanger Integrity Test | No cracks/leaks |  | Pass/Fail | Pass
Burner Ignition Time to Flame | Per mfr. spec |  | sec | Per mfr.
High-Limit Cutout Temp (verified) | Per nameplate |  | °F | Per nameplate
Supply Air Temp Rise (ΔT) | Per nameplate |  | °F | Per nameplate
© Your HVAC Co. ¦ Rogers, AR ¦ (555) 867-5309 ¦ www.yourhvac.com

## Deficiency Log & Closeout
Your HVAC Co. |  |  |  | START-UP DEFICIENCY LOG & PROJECT CLOSEOUT
Rogers, AR • (555) 867-5309 • www.yourhvac.com • service@yourhvac.com
⚠️ SECTION A — START-UP DEFICIENCIES & PUNCH LIST
Issue # | Date Found | Description of Deficiency | Found By | Responsible Party | Target Date | Status
1 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Accepted
2 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Accepted
3 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Accepted
4 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Accepted
5 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Accepted
6 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Accepted
7 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Accepted
8 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Accepted
9 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Accepted
10 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Accepted
11 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Accepted
12 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Accepted
13 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Accepted
14 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Accepted
15 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Accepted
16 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Accepted
17 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Accepted
18 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Accepted
19 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Accepted
20 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Accepted
21 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Accepted
22 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Accepted
23 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Accepted
24 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Accepted
25 | [5 empty] | ☐ Open ☐ In Progress ☐ Resolved ☐ Accepted
🎓 SECTION B — OWNER / OPERATOR TRAINING LOG
# | Training Topic | Date | Trainer Name | Attendees | Duration (hrs) | Sign-Off
1 | System Overview & Design Intent |  |  |  |  | ☐ Complete
2 | Equipment Operation & Controls Interface |  |  |  |  | ☐ Complete
3 | Thermostat / Zone Controller Operation |  |  |  |  | ☐ Complete
4 | Occupied / Unoccupied Scheduling |  |  |  |  | ☐ Complete
5 | Economizer & Outdoor Air Controls |  |  |  |  | ☐ Complete
6 | Filter Replacement Procedures & Schedule |  |  |  |  | ☐ Complete
7 | Preventive Maintenance Requirements |  |  |  |  | ☐ Complete
8 | Warranty Registration & Documentation |  |  |  |  | ☐ Complete
9 | Emergency Shut-Down Procedures |  |  |  |  | ☐ Complete
10 | BAS / DDC Alarm Response & Reset |  |  |  |  | ☐ Complete
✅ SECTION C — START-UP CLOSEOUT & SIGN-OFF
All Pre-Start-Up Checklist Items Passed? (Y/N):
All Safety Controls Tested & Verified? (Y/N):
All Measured Data Within Spec? (Y/N):
All Deficiencies Resolved or Accepted? (Y/N):
Owner / Operator Training Completed? (Y/N):
O&M Manuals Delivered to Owner? (Y/N):
Warranty Documents Submitted? (Y/N):
As-Built Drawings / Controls Diagrams Delivered? (Y/N):
🖊️ SECTION D — SIGNATURES
Lead Start-Up Technician Signature:
Print Name: |  | Date: |  | License #:
CxA / Commissioning Agent Signature:
Print Name: |  | Date: |  | Certification #:
Owner / Owner's Representative:
Print Name: |  | Date: |  | Title:
General Contractor Representative:
Print Name: |  | Date: |  | Title:
© Your HVAC Co. ¦ Rogers, AR ¦ (555) 867-5309 ¦ www.yourhvac.com