## Service Info & Customer Record
Your HVAC Co. | HVAC CLEAN & CHECK SERVICE CHECKLIST
Rogers, AR • (555) 867-5309 • www.yourhvac.com • service@yourhvac.com
📋 SECTION 1 — CUSTOMER & SITE INFORMATION
Customer Name:
Service Address:
City / State / ZIP:
Customer Phone:
Customer Email:
Property Type:
Service Agreement / Contract #:
Work Order / Dispatch #:
Service Type (select):
Preferred Service Window:
Gate Code / Access Instructions:
Special Instructions / Hazards:
🏷️ SECTION 2 — EQUIPMENT BEING SERVICED
Unit Tag / Equipment ID:
Equipment Type / Category:
Manufacturer:
Model Number:
Serial Number:
Year of Manufacture:
Voltage / Phase / Hz:
Refrigerant Type:
Cooling Capacity (Btuh / Tons):
Heating Capacity (Btuh / kW):
Location (rooftop / closet / attic / mechanical room):
Filter Size (W × H × D):
Filter MERV Rating:
Last Service Date:
Last Filter Change Date:
Warranty Status (in / out of warranty):
Maintenance Agreement Active? (Y/N):
👷 SECTION 3 — TECHNICIAN & SERVICE RECORD
Technician Name:
Technician License / Cert #:
Service Date:
Arrival Time:
Departure Time:
Ambient Temperature (°F):
Ambient Relative Humidity (%):
Customer Present During Service? (Y/N):
Customer Complaint / Reported Issues:
Previous Work Order Notes Reviewed? (Y/N):
© Your HVAC Co. ¦ Rogers, AR ¦ (555) 867-5309 ¦ www.yourhvac.com

## Indoor Unit Clean & Check
Your HVAC Co. |  |  |  | INDOOR UNIT — CLEAN & CHECK CHECKLIST
Rogers, AR • (555) 867-5309 • www.yourhvac.com • service@yourhvac.com
📝 INDOOR UNIT HEADER
Unit Tag / Equipment ID:
Location / Zone:
Manufacturer / Model:
Service Date & Technician:
🌀 CC-A — AIR HANDLER / FAN COIL MECHANICAL INSPECTION & CLEANING
# | Clean & Check Task | Pass | Fail | N/A | Condition / Reading | Tech Notes
1 | Filter inspected — condition noted; replaced or cleaned per schedule | ☐ | ☐ | ☐
2 | Filter rack / housing inspected — no bypass gaps; sealed correctly | ☐ | ☐ | ☐
3 | Blower wheel inspected for dirt buildup, imbalance, and blade damage | ☐ | ☐ | ☐
4 | Blower wheel cleaned — debris removed; re-inspected after cleaning | ☐ | ☐ | ☐
5 | Blower housing interior cleaned — no mold, debris, or obstructions | ☐ | ☐ | ☐
6 | Blower motor inspected — bearings, shaft, and mounting secure | ☐ | ☐ | ☐
7 | Blower motor lubricated (if oil ports present — per mfr. spec) | ☐ | ☐ | ☐
8 | Blower motor amps measured and compared to nameplate FLA | ☐ | ☐ | ☐
9 | Belt drive inspected (if belt-drive unit) — tension and wear checked | ☐ | ☐ | ☐
10 | Belt replaced if glazed, cracked, or worn beyond tolerance | ☐ | ☐ | ☐
11 | Evaporator coil inspected — condition, debris, and fouling noted | ☐ | ☐ | ☐
12 | Evaporator coil cleaned — foaming coil cleaner applied and rinsed | ☐ | ☐ | ☐
13 | Evaporator coil fins straightened (fin comb used where needed) | ☐ | ☐ | ☐
14 | Evaporator coil drain pan inspected — standing water or algae noted | ☐ | ☐ | ☐
15 | Drain pan cleaned — algae, slime, and debris removed | ☐ | ☐ | ☐
16 | Condensate drain line flushed — clear flow verified | ☐ | ☐ | ☐
17 | Condensate P-trap inspected — water seal intact; no blockage | ☐ | ☐ | ☐
18 | Condensate overflow sensor tested — unit shuts down on water | ☐ | ☐ | ☐
19 | Air handler cabinet / casing inspected — no air leaks, damage, or rust | ☐ | ☐ | ☐
20 | All interior panels and access doors reinstalled and secured | ☐ | ☐ | ☐
🔲 CC-B — DUCTWORK & DIFFUSER VISIBLE INSPECTION
# | Clean & Check Task | Pass | Fail | N/A | Condition / Reading | Tech Notes
1 | Supply registers / diffusers inspected — no excessive dust or blockage | ☐ | ☐ | ☐
2 | Supply registers / diffusers cleaned — face plates wiped down | ☐ | ☐ | ☐
3 | Return grilles inspected — no blockage; adequate return area | ☐ | ☐ | ☐
4 | Return grilles cleaned — filter removed and grille vacuumed | ☐ | ☐ | ☐
5 | Accessible ductwork inspected — no disconnects, tears, or collapsed flex | ☐ | ☐ | ☐
6 | Duct insulation inspected — no damage, moisture, or missing sections | ☐ | ☐ | ☐
7 | Supply air temperature measured at each zone register (spot check) | ☐ | ☐ | ☐
8 | Static pressure at supply plenum measured and recorded | ☐ | ☐ | ☐
⚡ CC-C — INDOOR ELECTRICAL INSPECTION
# | Clean & Check Task | Pass | Fail | N/A | Condition / Reading | Tech Notes
1 | Disconnect switch (indoor) inspected — no corrosion or loose connections | ☐ | ☐ | ☐
2 | Control board inspected — no fault codes, burn marks, or damaged components | ☐ | ☐ | ☐
3 | All low-voltage wiring inspected — no fraying, corrosion, or loose terminals | ☐ | ☐ | ☐
4 | Contactor / relay inspected — contact points clean, no pitting or burning | ☐ | ☐ | ☐
5 | Capacitor (blower motor) inspected — no bulging, leaking, or swelling | ☐ | ☐ | ☐
6 | Capacitor tested with capacitor meter — within ±6% of rated µF | ☐ | ☐ | ☐
7 | Thermostat / zone controller inspected — battery replaced if low | ☐ | ☐ | ☐
8 | Thermostat setpoints and programming verified per owner preferences | ☐ | ☐ | ☐
9 | All electrical connections retorqued — loose terminals tightened | ☐ | ☐ | ☐
10 | Control compartment cleaned — dust and debris removed | ☐ | ☐ | ☐
© Your HVAC Co. ¦ Rogers, AR ¦ (555) 867-5309 ¦ www.yourhvac.com

## Outdoor Unit Clean & Check
Your HVAC Co. |  |  |  | OUTDOOR UNIT — CLEAN & CHECK CHECKLIST
Rogers, AR • (555) 867-5309 • www.yourhvac.com • service@yourhvac.com
📝 OUTDOOR UNIT HEADER
Unit Tag / Equipment ID:
Location (rooftop / ground / wall):
Manufacturer / Model:
Service Date & Technician:
🔩 CC-D — OUTDOOR UNIT MECHANICAL INSPECTION & CLEANING
# | Clean & Check Task | Pass | Fail | N/A | Condition / Reading | Tech Notes
1 | Unit surroundings inspected — ≥ 24 in. clearance on all sides verified | ☐ | ☐ | ☐
2 | Debris removed from around unit — leaves, grass, and mulch cleared | ☐ | ☐ | ☐
3 | Condenser coil inspected — fouling, bent fins, and damage noted | ☐ | ☐ | ☐
4 | Condenser coil cleaned — coil cleaner applied; rinsed top-down | ☐ | ☐ | ☐
5 | Condenser coil fins straightened — fin comb used where needed | ☐ | ☐ | ☐
6 | Condenser fan blade(s) inspected — no cracks, bends, or imbalance | ☐ | ☐ | ☐
7 | Condenser fan blade(s) cleaned — dirt and debris removed | ☐ | ☐ | ☐
8 | Condenser fan motor inspected — bearings, mounting, and shaft secure | ☐ | ☐ | ☐
9 | Condenser fan motor lubricated (if oil ports present — per mfr. spec) | ☐ | ☐ | ☐
10 | Condenser fan motor amps measured and compared to nameplate FLA | ☐ | ☐ | ☐
11 | Fan guard / grille inspected — no damage; properly secured | ☐ | ☐ | ☐
12 | Unit base pan inspected — standing water, rust, or debris noted | ☐ | ☐ | ☐
13 | Base pan drain holes clear — no blockage | ☐ | ☐ | ☐
14 | Refrigerant lines inspected — insulation condition, supports, no damage | ☐ | ☐ | ☐
15 | Service port caps reinstalled and hand-tight after inspection | ☐ | ☐ | ☐
16 | Unit mounting (pad / curb / brackets) inspected — secure and level | ☐ | ☐ | ☐
17 | Unit casing / cabinet inspected — no sharp edges, rust, or panel damage | ☐ | ☐ | ☐
18 | All panels and screws reinstalled after cleaning | ☐ | ☐ | ☐
⚡ CC-E — OUTDOOR ELECTRICAL INSPECTION
# | Clean & Check Task | Pass | Fail | N/A | Condition / Reading | Tech Notes
1 | Disconnect box inspected — no corrosion, water intrusion, or damage | ☐ | ☐ | ☐
2 | Disconnect fuses / breaker inspected — rated correctly; no signs of overheating | ☐ | ☐ | ☐
3 | Supply voltage measured at disconnect — within ±10% of nameplate | ☐ | ☐ | ☐
4 | Voltage imbalance calculated (3-phase) — ≤ 2% | ☐ | ☐ | ☐
5 | All power wiring connections inspected and retorqued | ☐ | ☐ | ☐
6 | Contactor inspected — contact points clean; no pitting, burning, or sticking | ☐ | ☐ | ☐
7 | Contactor coil voltage tested — energizes and releases correctly | ☐ | ☐ | ☐
8 | Contactor replaced if pitted, burned, or worn (note if replaced) | ☐ | ☐ | ☐
9 | Run capacitor (compressor) tested — within ±6% of rated µF | ☐ | ☐ | ☐
10 | Run capacitor (fan motor) tested — within ±6% of rated µF | ☐ | ☐ | ☐
11 | Start capacitor / hard-start kit inspected (if installed) | ☐ | ☐ | ☐
12 | Crankcase heater operation confirmed (if applicable) | ☐ | ☐ | ☐
13 | All low-voltage control wiring inspected — no corrosion or loose terminals | ☐ | ☐ | ☐
14 | Condenser electrical compartment cleaned — dust and debris removed | ☐ | ☐ | ☐
15 | All electrical covers and compartment panels reinstalled and secured | ☐ | ☐ | ☐
❄️ CC-F — REFRIGERANT SYSTEM & COMPRESSOR INSPECTION
# | Clean & Check Task | Pass | Fail | N/A | Condition / Reading | Tech Notes
1 | Refrigerant system operated in cooling mode — normal cycle confirmed | ☐ | ☐ | ☐
2 | Suction line temperature / pressure measured | ☐ | ☐ | ☐
3 | Discharge line temperature / pressure measured | ☐ | ☐ | ☐
4 | Evaporator superheat calculated — within spec for metering device | ☐ | ☐ | ☐
5 | Condenser subcooling calculated — within spec | ☐ | ☐ | ☐
6 | Refrigerant leak check performed — all joints, fittings, and coils | ☐ | ☐ | ☐
7 | Leak check method used documented (electronic / UV dye / bubble) | ☐ | ☐ | ☐
8 | Compressor amps measured — compared to nameplate RLA | ☐ | ☐ | ☐
9 | Compressor sound inspected — no liquid slugging, rattling, or grinding | ☐ | ☐ | ☐
10 | Compressor case temperature measured — within normal range | ☐ | ☐ | ☐
11 | Sight glass inspected — clear; no bubbles under steady-state conditions | ☐ | ☐ | ☐
12 | Filter dryer condition noted — replacement recommended if system opened | ☐ | ☐ | ☐
© Your HVAC Co. ¦ Rogers, AR ¦ (555) 867-5309 ¦ www.yourhvac.com

## Gas & Heat System Check
Your HVAC Co. |  |  |  | GAS & HEAT SYSTEM CLEAN & CHECK (IF APPLICABLE)
Rogers, AR • (555) 867-5309 • www.yourhvac.com • service@yourhvac.com
📝 GAS / HEAT HEADER — COMPLETE FOR GAS FURNACE OR HEAT PUMP HEAT
Unit Tag / Equipment ID:
Heat System Type (gas / HP / electric strip):
Manufacturer / Model:
Service Date & Technician:
🔥 CC-G — GAS FURNACE / HEAT SECTION INSPECTION & CLEANING
# | Clean & Check Task | Pass | Fail | N/A | Condition / Reading | Tech Notes
1 | Gas supply pressure verified at unit — within manufacturer specifications | ☐ | ☐ | ☐
2 | Gas manifold pressure verified (operating) — per nameplate | ☐ | ☐ | ☐
3 | Burners inspected — no rust, scale buildup, or flame impingement | ☐ | ☐ | ☐
4 | Burners cleaned — debris removed; flame pattern uniform after cleaning | ☐ | ☐ | ☐
5 | Ignitor inspected (hot surface or spark) — clean; no cracks or wear | ☐ | ☐ | ☐
6 | Ignitor microamps / resistance tested — within manufacturer spec | ☐ | ☐ | ☐
7 | Flame sensor cleaned — carbon deposits removed with fine steel wool | ☐ | ☐ | ☐
8 | Flame sensor microamps tested — within manufacturer spec (≥ 1.5 µA typical) | ☐ | ☐ | ☐
9 | Heat exchanger visually inspected — no cracks, holes, or perforations | ☐ | ☐ | ☐
10 | Heat exchanger integrity test performed (combustion air test / CO check) | ☐ | ☐ | ☐
11 | CO levels in supply air measured — less than 9 ppm in living space | ☐ | ☐ | ☐
12 | Flue gas temperature measured and recorded | ☐ | ☐ | ☐
13 | Flue / exhaust piping inspected — no blockage, corrosion, or disconnects | ☐ | ☐ | ☐
14 | Combustion air inlet inspected — no blockage, screen clear | ☐ | ☐ | ☐
15 | Inducer motor inspected — no noise, vibration, or bearing wear | ☐ | ☐ | ☐
16 | Inducer motor amps measured — within nameplate FLA | ☐ | ☐ | ☐
17 | Pressure switch hoses inspected — no cracks, kinks, or water | ☐ | ☐ | ☐
18 | Gas valve inspected — no leaks detected at valve body or connections | ☐ | ☐ | ☐
19 | Rollout switch / high-limit tested — trips and resets correctly | ☐ | ☐ | ☐
20 | Heating cycle run to completion — no nuisance faults or lockouts | ☐ | ☐ | ☐
21 | Temperature rise measured (ΔT) — within nameplate range | ☐ | ☐ | ☐
♨️ CC-H — HEAT PUMP HEATING MODE CHECK (IF APPLICABLE)
# | Clean & Check Task | Pass | Fail | N/A | Condition / Reading | Tech Notes
1 | Heat pump heating mode initiated — confirmed unit calls for heating | ☐ | ☐ | ☐
2 | Reversing valve energized — confirmed changeover to heating mode | ☐ | ☐ | ☐
3 | Suction and discharge pressures measured in heating mode | ☐ | ☐ | ☐
4 | Heating suction superheat measured — within spec | ☐ | ☐ | ☐
5 | Outdoor coil (evaporator in heat mode) inspected — no ice in non-defrost | ☐ | ☐ | ☐
6 | Defrost board inspected — no fault codes; defrost initiation reviewed | ☐ | ☐ | ☐
7 | Defrost cycle initiated manually — unit entered and exited defrost correctly | ☐ | ☐ | ☐
8 | Auxiliary / emergency electric heat strips inspected and tested | ☐ | ☐ | ☐
9 | Aux heat amps measured per strip — within rated ampacity | ☐ | ☐ | ☐
10 | Aux heat lockout setpoint verified — correct OAT lockout programmed | ☐ | ☐ | ☐
11 | Balance point / second-stage setpoint verified in controls | ☐ | ☐ | ☐
12 | Crankcase heater confirmed energized during off cycle | ☐ | ☐ | ☐
© Your HVAC Co. ¦ Rogers, AR ¦ (555) 867-5309 ¦ www.yourhvac.com

## Measured Data & Performance
Your HVAC Co. |  |  |  | MEASURED DATA & SYSTEM PERFORMANCE RECORD
Rogers, AR • (555) 867-5309 • www.yourhvac.com • service@yourhvac.com
⚡ SECTION A — ELECTRICAL MEASUREMENTS
Parameter | Nameplate / Spec | Measured Value | Unit | Tolerance | Status | Notes
Supply Voltage — L1 to L2 | Per nameplate ±10% |  | VAC | ±10%
Supply Voltage — L2 to L3 | Per nameplate ±10% |  | VAC | ±10%
Supply Voltage — L1 to L3 | Per nameplate ±10% |  | VAC | ±10%
Voltage Imbalance (3-phase) | ≤ 2% |  | % | ≤ 2%
Compressor Amps — L1 | ≤ RLA nameplate |  | Amps | ≤ RLA
Compressor Amps — L2 | ≤ RLA nameplate |  | Amps | ≤ RLA
Condenser Fan Motor Amps | ≤ FLA nameplate |  | Amps | ≤ FLA
Blower / AHU Motor Amps | ≤ FLA nameplate |  | Amps | ≤ FLA
Run Capacitor — Compressor (µF) | Per nameplate ±6% |  | µF | ±6%
Run Capacitor — Fan Motor (µF) | Per nameplate ±6% |  | µF | ±6%
🧊 SECTION B — REFRIGERANT SYSTEM MEASUREMENTS
Parameter | Design / Spec | Measured Value | Unit | Tolerance | Status | Notes
Refrigerant Type | Per nameplate |  | — | Exact match
Suction Pressure | Varies by ref. |  | psig | Per chart
Discharge Pressure | Varies by ref. |  | psig | Per chart
Saturated Suction Temp | Varies by ref. |  | °F | Per chart
Saturated Discharge Temp | Varies by ref. |  | °F | Per chart
Evaporator Superheat | 8–12°F (TXV) |  | °F | ±2°F
Condenser Subcooling | 10–15°F |  | °F | ±2°F
Suction Line Temp (actual) | Per design |  | °F | ±3°F
Liquid Line Temp (actual) | Per design |  | °F | ±3°F
Compressor Discharge Temp | < 225°F typical |  | °F | < 225°F
Evaporator Coil Delta-T | 16–22°F typical |  | °F | Per design
Compressor Amps (measured) | ≤ RLA nameplate |  | Amps | ≤ RLA
Refrigerant Leak Check Result | No leaks |  | Pass/Fail | No leaks
💨 SECTION C — AIRSIDE PERFORMANCE
Parameter | Design Value | Measured Value | Unit | % Deviation | Status | Notes
Total Supply CFM |  |  | CFM | ±10%
Total Return CFM |  |  | CFM | ±10%
Supply Static Pressure |  |  | in. w.c. | Per design
Return Static Pressure |  |  | in. w.c. | Per design
Total External Static Pressure |  |  | in. w.c. | ≤ unit ESP
Supply Air Temp — Cooling DB |  |  | °F | Per design
Return Air Temp — DB |  |  | °F | Per design
Return Air Temp — WB |  |  | °F | Per design
Mixed Air Temp (OA + RA) |  |  | °F | Calculated
Filter Pressure Drop (clean) |  |  | in. w.c. | Per mfr.
Supply Air Temp — Heating |  |  | °F | Per design
Temp Rise ΔT (gas heat) |  |  | °F | Per nameplate
🔥 SECTION D — GAS / COMBUSTION MEASUREMENTS (IF APPLICABLE)
Parameter | Nameplate / Spec | Measured Value | Unit | Tolerance | Status | Notes
Gas Supply Pressure (at unit) | Per nameplate |  | in. w.c. | Per mfr.
Gas Manifold Pressure (operating) | Per nameplate |  | in. w.c. | Per mfr.
Flue Gas Temperature | Per design |  | °F | Per design
CO in Flue (undiluted) | < 400 ppm |  | ppm CO | < 400 ppm
CO in Supply Air | < 9 ppm |  | ppm CO | < 9 ppm
Flame Sensor Signal (µA) | ≥ 1.5 µA typical |  | µA | Per mfr.
Ignitor Resistance | Per mfr. spec |  | Ohms | Per mfr.
Supply Air Temp Rise (ΔT) | Per nameplate |  | °F | Per nameplate
© Your HVAC Co. ¦ Rogers, AR ¦ (555) 867-5309 ¦ www.yourhvac.com

## Component Condition Ratings
Your HVAC Co. |  |  |  | COMPONENT CONDITION RATINGS & RECOMMENDATIONS
Rogers, AR • (555) 867-5309 • www.yourhvac.com • service@yourhvac.com
📊 CONDITION RATING LEGEND & INSTRUCTIONS
G = Good (no action) F = Fair (monitor / note) P = Poor (recommend replacement) N/A = Not applicable
🌀 INDOOR UNIT COMPONENTS
# | Component | Good | Fair | Poor | N/A | Action Required / Notes
1 | Air Filter | ☐ G | ☐ F | ☐ P | ☐ N/A
2 | Blower Wheel | ☐ G | ☐ F | ☐ P | ☐ N/A
3 | Blower Motor | ☐ G | ☐ F | ☐ P | ☐ N/A
4 | Blower Motor Capacitor | ☐ G | ☐ F | ☐ P | ☐ N/A
5 | Blower Belts (if applicable) | ☐ G | ☐ F | ☐ P | ☐ N/A
6 | Evaporator Coil | ☐ G | ☐ F | ☐ P | ☐ N/A
7 | Evaporator Coil Fins | ☐ G | ☐ F | ☐ P | ☐ N/A
8 | Drain Pan | ☐ G | ☐ F | ☐ P | ☐ N/A
9 | Condensate Drain Line | ☐ G | ☐ F | ☐ P | ☐ N/A
10 | Condensate P-Trap | ☐ G | ☐ F | ☐ P | ☐ N/A
11 | Condensate Overflow Sensor | ☐ G | ☐ F | ☐ P | ☐ N/A
12 | Control Board | ☐ G | ☐ F | ☐ P | ☐ N/A
13 | Contactor / Relay (indoor) | ☐ G | ☐ F | ☐ P | ☐ N/A
14 | Thermostat / Zone Controller | ☐ G | ☐ F | ☐ P | ☐ N/A
15 | Low-Voltage Wiring (indoor) | ☐ G | ☐ F | ☐ P | ☐ N/A
16 | Air Handler Cabinet / Casing | ☐ G | ☐ F | ☐ P | ☐ N/A
17 | Ductwork Connections (visible) | ☐ G | ☐ F | ☐ P | ☐ N/A
18 | Duct Insulation (visible) | ☐ G | ☐ F | ☐ P | ☐ N/A
19 | Supply Registers / Diffusers | ☐ G | ☐ F | ☐ P | ☐ N/A
20 | Return Grille(s) | ☐ G | ☐ F | ☐ P | ☐ N/A
🏠 OUTDOOR UNIT COMPONENTS
# | Component | Good | Fair | Poor | N/A | Action Required / Notes
1 | Condenser Coil | ☐ G | ☐ F | ☐ P | ☐ N/A
2 | Condenser Coil Fins | ☐ G | ☐ F | ☐ P | ☐ N/A
3 | Condenser Fan Blade(s) | ☐ G | ☐ F | ☐ P | ☐ N/A
4 | Condenser Fan Motor | ☐ G | ☐ F | ☐ P | ☐ N/A
5 | Condenser Fan Capacitor | ☐ G | ☐ F | ☐ P | ☐ N/A
6 | Compressor | ☐ G | ☐ F | ☐ P | ☐ N/A
7 | Compressor Capacitor (run) | ☐ G | ☐ F | ☐ P | ☐ N/A
8 | Start Capacitor / Hard-Start Kit | ☐ G | ☐ F | ☐ P | ☐ N/A
9 | Contactor | ☐ G | ☐ F | ☐ P | ☐ N/A
10 | Crankcase Heater | ☐ G | ☐ F | ☐ P | ☐ N/A
11 | Service Valves | ☐ G | ☐ F | ☐ P | ☐ N/A
12 | Filter Dryer | ☐ G | ☐ F | ☐ P | ☐ N/A
13 | Sight Glass | ☐ G | ☐ F | ☐ P | ☐ N/A
14 | Refrigerant Lines / Insulation | ☐ G | ☐ F | ☐ P | ☐ N/A
15 | Disconnect Box / Fusing | ☐ G | ☐ F | ☐ P | ☐ N/A
16 | Supply Wiring / Conduit (outdoor) | ☐ G | ☐ F | ☐ P | ☐ N/A
17 | Unit Cabinet / Casing | ☐ G | ☐ F | ☐ P | ☐ N/A
18 | Unit Mounting Pad / Curb | ☐ G | ☐ F | ☐ P | ☐ N/A
19 | Base Pan / Drain | ☐ G | ☐ F | ☐ P | ☐ N/A
20 | Fan Guard / Grille | ☐ G | ☐ F | ☐ P | ☐ N/A
🔥 GAS / HEAT COMPONENTS (IF APPLICABLE)
# | Component | Good | Fair | Poor | N/A | Action Required / Notes
1 | Gas Burners | ☐ G | ☐ F | ☐ P | ☐ N/A
2 | Ignitor | ☐ G | ☐ F | ☐ P | ☐ N/A
3 | Flame Sensor | ☐ G | ☐ F | ☐ P | ☐ N/A
4 | Heat Exchanger (visual) | ☐ G | ☐ F | ☐ P | ☐ N/A
5 | Inducer Motor | ☐ G | ☐ F | ☐ P | ☐ N/A
6 | Flue / Exhaust Piping | ☐ G | ☐ F | ☐ P | ☐ N/A
7 | Combustion Air Inlet | ☐ G | ☐ F | ☐ P | ☐ N/A
8 | Pressure Switch Hoses | ☐ G | ☐ F | ☐ P | ☐ N/A
9 | Gas Valve | ☐ G | ☐ F | ☐ P | ☐ N/A
10 | Rollout Switch | ☐ G | ☐ F | ☐ P | ☐ N/A
11 | High-Limit Switch | ☐ G | ☐ F | ☐ P | ☐ N/A
12 | Aux / Emergency Heat Strips | ☐ G | ☐ F | ☐ P | ☐ N/A
13 | Defrost Board (HP units) | ☐ G | ☐ F | ☐ P | ☐ N/A
14 | Reversing Valve (HP units) | ☐ G | ☐ F | ☐ P | ☐ N/A
© Your HVAC Co. ¦ Rogers, AR ¦ (555) 867-5309 ¦ www.yourhvac.com

## Service Summary & Closeout
Your HVAC Co. |  |  |  | SERVICE SUMMARY, RECOMMENDATIONS & CLOSEOUT
Rogers, AR • (555) 867-5309 • www.yourhvac.com • service@yourhvac.com
🔧 SECTION A — PARTS & MATERIALS USED THIS SERVICE
# | Part Number | Description | Qty | Unit Cost | Total Cost | Warranty / Notes
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
📋 SECTION B — SERVICE RECOMMENDATIONS & FINDINGS
# | Date | Recommendation / Finding | Priority | Est. Cost | Quoted | Accepted
1 |  |  | High
2 |  |  | High
3 |  |  | High
4 |  |  | Medium
5 |  |  | Medium
6 |  |  | Medium
7 |  |  | Low
8 |  |  | Low
9 |  |  | Low
10 |  |  | Low
✅ SECTION C — SERVICE CLOSEOUT VERIFICATION
All clean & check tasks completed per checklist? (Y/N):
All measured data recorded and within specification? (Y/N):
Refrigerant leak check performed and passed? (Y/N):
Filter replaced or cleaned? (Y/N / customer declined):
All panels and access doors reinstalled? (Y/N):
Site clean — no tools or debris left behind? (Y/N):
Customer informed of findings and recommendations? (Y/N):
Recommendations quoted and provided in writing? (Y/N):
Service report copy provided to customer? (Y/N):
Service report uploaded to company system? (Y/N):
Follow-up work order created for open items? (Y/N / N/A):
📝 SECTION D — TECHNICIAN NOTES & ADDITIONAL OBSERVATIONS
Technician notes / additional observations:
🖊️ SECTION E — SERVICE SIGN-OFF SIGNATURES
Lead Technician Signature:
Print Name: |  | Date: |  | License / Cert #:
Customer / Owner Signature:
Print Name: |  | Date: |  | Title:
© Your HVAC Co. ¦ Rogers, AR ¦ (555) 867-5309 ¦ www.yourhvac.com