## RTU Service Info & Equipment
Your HVAC Co. | ROOFTOP UNIT MAINTENANCE CHECKLIST
Rogers, AR • (555) 867-5309 • www.yourhvac.com • service@yourhvac.com
📋 SECTION 1 — CUSTOMER & SITE INFORMATION
Customer / Building Owner Name:
Facility Name / Building ID:
Service Address:
City / State / ZIP:
Customer Phone:
Customer Email:
Facility Manager / Contact:
FM Phone & Email:
Property Type / Occupancy:
Service Agreement / Contract #:
Work Order / Dispatch #:
Maintenance Frequency (quarterly / semi-annual / annual):
Roof Access Method (hatch / ladder / stair tower):
Roof Safety Requirements (tie-off / spotter):
Special Access / Permit Required? (Y/N):
Special Instructions / Hazards:
🏷️ SECTION 2 — RTU EQUIPMENT NAMEPLATE & IDENTIFICATION
Unit Tag / Equipment ID:
RTU Type (cooling only / heat pump / gas heat / electric heat):
Manufacturer:
Model Number:
Serial Number:
Year of Manufacture:
Voltage / Phase / Hz:
MCA (Min. Circuit Ampacity):
MOCP (Max. Overcurrent Protection):
Refrigerant Type:
Cooling Capacity (Btuh / Tons):
Heating Capacity (Btuh / kW / MBH):
Seasonal Efficiency (SEER2 / EER2 / AFUE / COP):
Supply CFM (design):
Total External Static Pressure (design):
Number of Compressors / Stages:
Number of Refrigerant Circuits:
Economizer Type (none / dry-bulb / enthalpy / differential):
BAS / DDC Controller Model:
Filter Size(s) and MERV Rating:
Curb Type / Dimensions:
Warranty Expiration Date:
Last PM Date:
Next PM Due Date:
👷 SECTION 3 — TECHNICIAN & SERVICE RECORD
Lead Technician Name:
Tech License / EPA Cert #:
Assisting Technician (if applicable):
Service Date:
Arrival Time:
Departure Time:
Ambient Temperature at Service (°F):
Ambient Relative Humidity (%):
Wind Speed / Conditions (rooftop):
Customer / FM Present? (Y/N):
Customer Complaint / Reported Issues:
Previous Work Order Notes Reviewed? (Y/N):
BAS / DDC Online at Arrival? (Y/N):
Active Fault Codes at Arrival (list):
© Your HVAC Co. ¦ Rogers, AR ¦ (555) 867-5309 ¦ www.yourhvac.com

## Rooftop Safety & Structural
Your HVAC Co. |  |  |  | ROOFTOP SAFETY & STRUCTURAL INSPECTION
Rogers, AR • (555) 867-5309 • www.yourhvac.com • service@yourhvac.com
📝 SECTION HEADER
Unit Tag / Equipment ID:
Service Date & Technician:
🦺 RS-A — ROOFTOP SAFETY VERIFICATION (COMPLETE BEFORE ACCESSING ROOF)
# | Safety Task / Verification | Pass | Fail | N/A | Observed / Notes | Tech Notes
1 | Fall protection equipment inspected — harness, lanyard, and anchor points verified | ☐ | ☐ | ☐
2 | Roof anchor / tie-off points rated and suitable for fall arrest confirmed | ☐ | ☐ | ☐
3 | Roof access hatch / ladder inspected — no damage, secure, and properly latched | ☐ | ☐ | ☐
4 | Roof surface inspected before walking — no ponding water, ice, or unstable areas | ☐ | ☐ | ☐
5 | All personnel on roof briefed on hazards and emergency procedures | ☐ | ☐ | ☐
6 | Hot work permit obtained if brazing / torch work required | ☐ | ☐ | ☐
7 | Permit-required confined space entry procedures reviewed (if applicable) | ☐ | ☐ | ☐
8 | Lockout / tagout (LOTO) equipment available and used before electrical work | ☐ | ☐ | ☐
9 | Weather check performed — work suspended if lightning, high winds, or icing | ☐ | ☐ | ☐
10 | Tools and materials secured against wind — no loose items on roof | ☐ | ☐ | ☐
11 | Roof drains / scuppers near unit inspected — not blocked by tools or debris | ☐ | ☐ | ☐
🏗️ RS-B — STRUCTURAL, CURB & MOUNTING INSPECTION
# | Structural Task / Verification | Pass | Fail | N/A | Observed / Notes | Tech Notes
1 | Unit curb inspected — no rust, rot, or structural deterioration | ☐ | ☐ | ☐
2 | Curb-to-deck attachment points inspected — no loose fasteners or separation | ☐ | ☐ | ☐
3 | Curb gasket / roof membrane seal inspected — no gaps, tears, or exposed flashing | ☐ | ☐ | ☐
4 | Roof membrane around curb inspected — no blisters, cracking, or open seams | ☐ | ☐ | ☐
5 | Unit mounting bolts / hardware inspected — all present, not corroded, torqued | ☐ | ☐ | ☐
6 | Unit level verified — no significant racking or settling since last PM | ☐ | ☐ | ☐
7 | Vibration isolators (if installed) inspected — no deterioration or collapse | ☐ | ☐ | ☐
8 | Flexible duct connectors at supply and return openings inspected — no tears or gaps | ☐ | ☐ | ☐
9 | Supply and return duct transitions inspected — insulation intact, no air leaks | ☐ | ☐ | ☐
10 | Roof penetrations for refrigerant lines, conduit, and drain inspected — sealed | ☐ | ☐ | ☐
11 | Refrigerant line insulation on roof inspected — no UV damage, missing sections | ☐ | ☐ | ☐
12 | Condensate line routing on roof inspected — not ponding on membrane | ☐ | ☐ | ☐
13 | Unit clearances from roof edge, parapet, and other equipment verified | ☐ | ☐ | ☐
14 | Bird / pest screening on all openings inspected — intact, no nesting evidence | ☐ | ☐ | ☐
© Your HVAC Co. ¦ Rogers, AR ¦ (555) 867-5309 ¦ www.yourhvac.com

## Airside & Filtration
Your HVAC Co. |  |  |  | AIRSIDE, FILTRATION & ECONOMIZER MAINTENANCE
Rogers, AR • (555) 867-5309 • www.yourhvac.com • service@yourhvac.com
📝 SECTION HEADER
Unit Tag / Equipment ID:
Service Date & Technician:
🔲 AS-A — FILTRATION INSPECTION & SERVICE
# | Task / Verification | Pass | Fail | N/A | Condition / Reading | Tech Notes
1 | Filter section access panels opened and inspected — no bypass air leaks | ☐ | ☐ | ☐
2 | Filters removed — condition documented (light / moderate / heavy loading) | ☐ | ☐ | ☐
3 | Filter quantity, size, and MERV rating verified against unit specification | ☐ | ☐ | ☐
4 | Filter rack / housing cleaned — loose debris vacuumed | ☐ | ☐ | ☐
5 | Filter bypass seals / gaskets inspected — replaced if damaged | ☐ | ☐ | ☐
6 | New filters installed — correct size and MERV rating confirmed | ☐ | ☐ | ☐
7 | Filter track / channel seating verified — no gaps around filter face | ☐ | ☐ | ☐
8 | Filter gauge / magnehelic (if installed) reset and reading noted after install | ☐ | ☐ | ☐
9 | Filter pressure drop measured (clean) — within manufacturer specification | ☐ | ☐ | ☐
10 | Filter change date and MERV rating logged on unit service label | ☐ | ☐ | ☐
🌀 AS-B — SUPPLY FAN, DRIVE & MOTOR INSPECTION
# | Task / Verification | Pass | Fail | N/A | Condition / Reading | Tech Notes
1 | Supply fan section accessed — shipping blocks / tie-downs absent (new unit only) | ☐ | ☐ | ☐
2 | Blower wheel inspected — no dirt buildup, imbalance, blade damage, or rust | ☐ | ☐ | ☐
3 | Blower wheel cleaned if fouled — re-inspected after cleaning | ☐ | ☐ | ☐
4 | Blower housing interior cleaned — no debris, mold, or obstructions | ☐ | ☐ | ☐
5 | Supply fan motor inspected — bearings, shaft, mounting bracket secure | ☐ | ☐ | ☐
6 | Supply fan motor lubricated (if oil ports present — per mfr. spec) | ☐ | ☐ | ☐
7 | Supply fan motor amps measured — recorded and compared to nameplate FLA | ☐ | ☐ | ☐
8 | VFD (if installed) inspected — no fault codes; parameters verified | ☐ | ☐ | ☐
9 | VFD cooling fan and filter cleaned (if VFD installed) | ☐ | ☐ | ☐
10 | Belt drive (if belt-drive unit): tension checked per mfr. spec | ☐ | ☐ | ☐
11 | Belt drive: belt inspected — no cracking, glazing, or excessive wear | ☐ | ☐ | ☐
12 | Belt drive: belt replaced if worn beyond tolerance — size and type noted | ☐ | ☐ | ☐
13 | Belt drive: sheave / pulley inspected — alignment and wear verified | ☐ | ☐ | ☐
14 | Belt drive: motor and blower sheave set screws / keyways verified tight | ☐ | ☐ | ☐
15 | Direct drive (if applicable): flexible coupling inspected for wear | ☐ | ☐ | ☐
16 | Fan rotation direction verified (correct rotation confirmed after any service) | ☐ | ☐ | ☐
🌬️ AS-C — ECONOMIZER INSPECTION & CALIBRATION
# | Task / Verification | Pass | Fail | N/A | Condition / Reading | Tech Notes
1 | Economizer type confirmed (none / dry-bulb / enthalpy / differential enthalpy) | ☐ | ☐ | ☐
2 | Outdoor air damper blades inspected — no cracks, warping, or binding | ☐ | ☐ | ☐
3 | OA damper blade linkage and shaft inspected — no looseness or corrosion | ☐ | ☐ | ☐
4 | OA damper actuator inspected — proper mounting, shaft tight | ☐ | ☐ | ☐
5 | OA damper actuator stroked full open (0–100%) — smooth travel confirmed | ☐ | ☐ | ☐
6 | OA damper actuator stroked to minimum position — min. OA % verified | ☐ | ☐ | ☐
7 | Return air damper blades and linkage inspected — no binding | ☐ | ☐ | ☐
8 | Return air damper actuator inspected and operation verified | ☐ | ☐ | ☐
9 | Exhaust / relief damper blades and operation inspected | ☐ | ☐ | ☐
10 | Dry-bulb sensor (OAT) inspected and calibrated (if dry-bulb economizer) | ☐ | ☐ | ☐
11 | Enthalpy sensor / controller inspected and calibrated (if enthalpy economizer) | ☐ | ☐ | ☐
12 | Differential enthalpy / return air sensor calibrated (if diff. enthalpy unit) | ☐ | ☐ | ☐
13 | Economizer controls verified — unit opens on free-cooling command | ☐ | ☐ | ☐
14 | Economizer 100% open position verified — supply air matches design CFM | ☐ | ☐ | ☐
15 | Economizer minimum position verified — OA CFM meets ventilation code | ☐ | ☐ | ☐
16 | High-limit setpoint verified — economizer closes at correct OAT or enthalpy | ☐ | ☐ | ☐
17 | Economizer fault / fault codes checked on BAS — no active faults | ☐ | ☐ | ☐
18 | Economizer hood / weather hood inspected — no damage or bird screen issues | ☐ | ☐ | ☐
19 | Bird screen on OA intake inspected — clean and undamaged | ☐ | ☐ | ☐
© Your HVAC Co. ¦ Rogers, AR ¦ (555) 867-5309 ¦ www.yourhvac.com

## Refrigerant System
Your HVAC Co. |  |  |  | REFRIGERANT SYSTEM MAINTENANCE & INSPECTION
Rogers, AR • (555) 867-5309 • www.yourhvac.com • service@yourhvac.com
📝 SECTION HEADER
Unit Tag / Equipment ID:
Service Date & Technician:
Number of Refrigerant Circuits:
Refrigerant Type:
🏠 RF-A — CONDENSER SECTION CLEANING & INSPECTION
# | Task / Verification | Pass | Fail | N/A | Condition / Reading | Tech Notes
1 | Condenser section access panels opened and inspected | ☐ | ☐ | ☐
2 | Condenser coil(s) inspected — fouling, fin damage, and corrosion noted (all circuits) | ☐ | ☐ | ☐
3 | Condenser coil(s) cleaned — coil cleaner applied and thoroughly rinsed top-down | ☐ | ☐ | ☐
4 | Condenser coil fins straightened — fin comb used on all damaged sections | ☐ | ☐ | ☐
5 | Condenser fan blades inspected (all fans) — no cracks, bends, or imbalance | ☐ | ☐ | ☐
6 | Condenser fan blades cleaned — debris and dirt removed | ☐ | ☐ | ☐
7 | Condenser fan motors inspected (all motors) — bearings, mounting, shaft secure | ☐ | ☐ | ☐
8 | Condenser fan motors lubricated (if oil ports present — per mfr. spec) | ☐ | ☐ | ☐
9 | Condenser fan motor amps measured (all motors) — compared to nameplate FLA | ☐ | ☐ | ☐
10 | Fan blade pitch verified (adjustable-pitch fans) — correct per balancing report | ☐ | ☐ | ☐
11 | Condenser section base pan inspected — debris, standing water, rust noted | ☐ | ☐ | ☐
12 | Base pan drain holes clear — no blockage or calcium buildup | ☐ | ☐ | ☐
13 | Unit disconnect(s) in condenser section inspected — corrosion and connection check | ☐ | ☐ | ☐
14 | All condenser section panels reinstalled and secured after service | ☐ | ☐ | ☐
🧊 RF-B — EVAPORATOR COIL, DRAIN PAN & CONDENSATE SYSTEM
# | Task / Verification | Pass | Fail | N/A | Condition / Reading | Tech Notes
1 | Evaporator section accessed — coil face inspected for fouling and damage | ☐ | ☐ | ☐
2 | Evaporator coil cleaned if needed — foaming coil cleaner applied and rinsed | ☐ | ☐ | ☐
3 | Evaporator coil fins inspected and straightened where bent | ☐ | ☐ | ☐
4 | Drain pan inspected — standing water, algae, slime, or debris noted | ☐ | ☐ | ☐
5 | Drain pan cleaned — all algae and buildup removed | ☐ | ☐ | ☐
6 | Condensate drain line flushed — clear flow confirmed at discharge | ☐ | ☐ | ☐
7 | Condensate drain line trap inspected — water seal intact, no blockage | ☐ | ☐ | ☐
8 | Condensate overflow switch tested — unit shuts down on high water | ☐ | ☐ | ☐
9 | Condensate piping on roof inspected — no sags, blockages, or ponding issues | ☐ | ☐ | ☐
10 | Evaporator coil entering air temperature measured | ☐ | ☐ | ☐
11 | Evaporator coil leaving air temperature measured — delta-T calculated | ☐ | ☐ | ☐
❄️ RF-C — REFRIGERANT CIRCUIT INSPECTION & LEAK CHECK
# | Task / Verification | Pass | Fail | N/A | Condition / Reading | Tech Notes
1 | Refrigerant type confirmed per unit nameplate — no unauthorized substitutions | ☐ | ☐ | ☐
2 | All service valve caps present — caps removed, valve positions checked | ☐ | ☐ | ☐
3 | Electronic leak detector used — all joints, coils, valves, and fittings checked | ☐ | ☐ | ☐
4 | Leak check results documented — location and severity of any leak noted | ☐ | ☐ | ☐
5 | Refrigerant pressures checked (all circuits) — suction and discharge recorded | ☐ | ☐ | ☐
6 | Refrigerant charge assessed against operating conditions — no top-off without diagnosis | ☐ | ☐ | ☐
7 | Sight glass inspected (all circuits) — clear, no bubbles at steady state | ☐ | ☐ | ☐
8 | Suction line insulation on all circuits inspected — no missing or wet sections | ☐ | ☐ | ☐
9 | Liquid line insulation inspected where required | ☐ | ☐ | ☐
10 | TXV / EEV operation verified — superheat stable and within spec | ☐ | ☐ | ☐
11 | Filter drier condition noted — replacement recommended if system was opened | ☐ | ☐ | ☐
12 | All service port Schrader cores confirmed installed — caps replaced | ☐ | ☐ | ☐
13 | Compressor(s) sound inspected — no liquid slugging, rattling, or grinding | ☐ | ☐ | ☐
14 | Compressor case temperature measured (all compressors) | ☐ | ☐ | ☐
15 | Oil sight glass inspected (if oil-sight-glass equipped) — oil level acceptable | ☐ | ☐ | ☐
16 | Crankcase heater(s) confirmed energized during off cycle | ☐ | ☐ | ☐
© Your HVAC Co. ¦ Rogers, AR ¦ (555) 867-5309 ¦ www.yourhvac.com

## Gas Heat & Electrical
Your HVAC Co. |  |  |  | GAS HEAT SECTION & ELECTRICAL MAINTENANCE
Rogers, AR • (555) 867-5309 • www.yourhvac.com • service@yourhvac.com
📝 SECTION HEADER
Unit Tag / Equipment ID:
Heat Type (gas / HP / electric strip):
Number of Gas Stages / Heat Sections:
Service Date & Technician:
🔥 GH-A — GAS HEAT SECTION MAINTENANCE & INSPECTION
# | Task / Verification | Pass | Fail | N/A | Condition / Reading | Tech Notes
1 | Gas heat section access panel opened — no evidence of heat damage, soot, or rollout | ☐ | ☐ | ☐
2 | Gas supply pressure measured at unit — within manufacturer spec | ☐ | ☐ | ☐
3 | Gas manifold pressure verified per stage — within nameplate spec | ☐ | ☐ | ☐
4 | Burner assemblies removed and inspected — rust, scale, or orifice buildup noted | ☐ | ☐ | ☐
5 | Burner assemblies cleaned — ports clear, flame pattern uniform after reinstall | ☐ | ☐ | ☐
6 | Heat exchanger visually inspected — no cracks, holes, or burn-through (all sections) | ☐ | ☐ | ☐
7 | Heat exchanger combustion-side inspected with mirror / camera (if accessible) | ☐ | ☐ | ☐
8 | CO level in supply air stream measured — less than 9 ppm acceptable | ☐ | ☐ | ☐
9 | CO in flue gas measured (undiluted) — less than 400 ppm acceptable | ☐ | ☐ | ☐
10 | Flue temperature measured and recorded | ☐ | ☐ | ☐
11 | Flue / exhaust vent pipe inspected at unit connection — no corrosion or leaks | ☐ | ☐ | ☐
12 | Flue gas cap / rain hood on RTU top inspected — clear, no bird nesting | ☐ | ☐ | ☐
13 | Inducer motor inspected — no abnormal noise, bearing wear, or vibration | ☐ | ☐ | ☐
14 | Inducer motor amps measured — within nameplate FLA | ☐ | ☐ | ☐
15 | Inducer wheel cleaned if fouled | ☐ | ☐ | ☐
16 | Pressure switch hoses inspected — no cracks, kinks, moisture, or disconnects | ☐ | ☐ | ☐
17 | Pressure switch operation verified — locks out on blocked-flue simulation | ☐ | ☐ | ☐
18 | Ignitor type noted (hot surface / spark); inspected and tested | ☐ | ☐ | ☐
19 | Ignitor resistance or microamps measured — within manufacturer spec | ☐ | ☐ | ☐
20 | Flame sensor cleaned — carbon deposits removed with fine steel wool | ☐ | ☐ | ☐
21 | Flame sensor microamps measured — ≥ 1.5 µA typical; within mfr. spec | ☐ | ☐ | ☐
22 | Gas valve inspected — no leaks at body, inlet, outlet, or manifold connections | ☐ | ☐ | ☐
23 | Rollout switch tested — trips correctly; manual reset performed and documented | ☐ | ☐ | ☐
24 | High-limit switch tested — trips and resets correctly | ☐ | ☐ | ☐
25 | Temperature rise (ΔT) measured — within nameplate range | ☐ | ☐ | ☐
26 | Full heating cycle run to completion — no fault codes or nuisance lockouts | ☐ | ☐ | ☐
⚡ GH-B — ELECTRICAL SYSTEM INSPECTION & MAINTENANCE
# | Task / Verification | Pass | Fail | N/A | Condition / Reading | Tech Notes
1 | Main RTU disconnect(s) inspected — no corrosion, water, or heat damage | ☐ | ☐ | ☐
2 | Disconnect fuse(s) / breaker inspected — rated per MCA/MOCP; no overheating | ☐ | ☐ | ☐
3 | Supply voltage measured at disconnect — within ±10% of nameplate | ☐ | ☐ | ☐
4 | Voltage imbalance calculated (3-phase) — ≤ 2% | ☐ | ☐ | ☐
5 | All power wiring inspected and connections retorqued to spec | ☐ | ☐ | ☐
6 | Conduit, fittings, and wire management inspected — no damage or water entry | ☐ | ☐ | ☐
7 | Main contactor(s) inspected — contacts clean, no pitting, burning, or sticking | ☐ | ☐ | ☐
8 | Contactor coil voltage tested — energizes and releases correctly | ☐ | ☐ | ☐
9 | Compressor run capacitor(s) tested — within ±6% of rated µF (all circuits) | ☐ | ☐ | ☐
10 | Fan motor run capacitor(s) tested — within ±6% of rated µF | ☐ | ☐ | ☐
11 | Start capacitor / hard-start kit inspected (if installed) | ☐ | ☐ | ☐
12 | Control board(s) inspected — no fault codes, burn marks, or damaged components | ☐ | ☐ | ☐
13 | All low-voltage control wiring inspected — no corrosion, fraying, or loose terminals | ☐ | ☐ | ☐
14 | Terminal strips inspected and retorqued — no loose or overheated terminals | ☐ | ☐ | ☐
15 | BAS / DDC controller inspected — firmware current, no active faults | ☐ | ☐ | ☐
16 | All relay, transformer, and fuse ratings verified per control schematic | ☐ | ☐ | ☐
17 | Electrical compartments cleaned — dust, debris, and insect nests removed | ☐ | ☐ | ☐
18 | All electrical panels, covers, and access doors reinstalled and secured | ☐ | ☐ | ☐
© Your HVAC Co. ¦ Rogers, AR ¦ (555) 867-5309 ¦ www.yourhvac.com

## Measured Data & Performance
Your HVAC Co. |  |  |  | RTU MEASURED DATA & PERFORMANCE RECORD
Rogers, AR • (555) 867-5309 • www.yourhvac.com • service@yourhvac.com
📝 DATA SESSION HEADER
Unit Tag / Equipment ID:
Service Date & Technician:
OAT (°F):
OA RH (%):
Number of Circuits:
⚡ SECTION A — ELECTRICAL MEASUREMENTS
Parameter | Nameplate / Spec | Measured Value | Unit | Tolerance | Status | Notes
Supply Voltage — L1 to L2 | Per nameplate ±10% |  | VAC | ±10%
Supply Voltage — L2 to L3 | Per nameplate ±10% |  | VAC | ±10%
Supply Voltage — L1 to L3 | Per nameplate ±10% |  | VAC | ±10%
Voltage Imbalance | ≤ 2% |  | % | ≤ 2%
Compressor Amps — Circuit 1 (L1) | ≤ RLA nameplate |  | Amps | ≤ RLA
Compressor Amps — Circuit 1 (L2) | ≤ RLA nameplate |  | Amps | ≤ RLA
Compressor Amps — Circuit 2 (L1) | ≤ RLA nameplate |  | Amps | ≤ RLA (if applicable)
Compressor Amps — Circuit 2 (L2) | ≤ RLA nameplate |  | Amps | ≤ RLA (if applicable)
Supply Fan Motor Amps | ≤ FLA nameplate |  | Amps | ≤ FLA
Condenser Fan 1 Amps | ≤ FLA nameplate |  | Amps | ≤ FLA
Condenser Fan 2 Amps (if appl.) | ≤ FLA nameplate |  | Amps | ≤ FLA
Condenser Fan 3 Amps (if appl.) | ≤ FLA nameplate |  | Amps | ≤ FLA
Total Unit Amps | ≤ MCA |  | Amps | ≤ MCA
Run Cap — Compressor 1 (µF) | Per nameplate ±6% |  | µF | ±6%
Run Cap — Compressor 2 (µF) | Per nameplate ±6% |  | µF | ±6% (if appl.)
Run Cap — Fan Motor(s) (µF) | Per nameplate ±6% |  | µF | ±6%
🧊 SECTION B — REFRIGERANT MEASUREMENTS (RECORD PER CIRCUIT)
Parameter | Circuit 1 | Circuit 2 | Unit | Tolerance | Status | Notes
Refrigerant Type | Per nameplate | Per nameplate | — | Exact match
Suction Pressure |  |  | psig | Per chart
Discharge Pressure |  |  | psig | Per chart
Saturated Suction Temp |  |  | °F | Per chart
Saturated Discharge Temp |  |  | °F | Per chart
Evaporator Superheat | 8–12°F (TXV) | 8–12°F (TXV) | °F | ±2°F
Condenser Subcooling | 10–15°F | 10–15°F | °F | ±2°F
Suction Line Temp (actual) |  |  | °F | ±3°F
Liquid Line Temp (actual) |  |  | °F | ±3°F
Compressor Discharge Temp | < 225°F | < 225°F | °F | < 225°F
Evap. Coil Delta-T | 16–22°F typical | 16–22°F typical | °F | Per design
Leak Check Result | No leaks | No leaks | Pass/Fail | No leaks
💨 SECTION C — AIRSIDE PERFORMANCE
Parameter | Design Value | Measured Value | Unit | % Deviation | Status | Notes
Total Supply CFM |  |  | CFM | ±10%
Total Return CFM |  |  | CFM | ±10%
Outdoor Air CFM (min.) |  |  | CFM | ±10%
Economizer OA CFM (full open) |  |  | CFM | Per design
Supply Static Pressure |  |  | in. w.c. | Per design
Return Static Pressure |  |  | in. w.c. | Per design
Total External Static Pressure |  |  | in. w.c. | ≤ unit ESP
Filter Pressure Drop (clean) |  |  | in. w.c. | Per mfr.
Supply Air Temp — Cooling DB |  |  | °F | Per design
Supply Air Temp — Heating |  |  | °F | Per design
Return Air Temp — DB |  |  | °F | Per design
Return Air Temp — WB |  |  | °F | Per design
Mixed Air Temp (OA + RA) |  |  | °F | Calculated
Temp Rise ΔT (gas heat) |  |  | °F | Per nameplate
🔥 SECTION D — GAS / COMBUSTION MEASUREMENTS (IF APPLICABLE)
Parameter | Nameplate / Spec | Measured Value | Unit | Tolerance | Status | Notes
Gas Supply Pressure at Unit | Per nameplate |  | in. w.c. | Per mfr.
Gas Manifold Pressure — Stage 1 | Per nameplate |  | in. w.c. | Per mfr.
Gas Manifold Pressure — Stage 2 | Per nameplate |  | in. w.c. | Per mfr. (if appl.)
Flue Gas Temperature | Per design |  | °F | Per design
CO in Flue (undiluted) | < 400 ppm |  | ppm CO | < 400 ppm
CO in Supply Air Stream | < 9 ppm |  | ppm CO | < 9 ppm
Flame Sensor Signal (µA) | ≥ 1.5 µA |  | µA | Per mfr.
Ignitor Resistance | Per mfr. spec |  | Ohms | Per mfr.
Inducer Motor Amps | ≤ FLA nameplate |  | Amps | ≤ FLA
Temperature Rise ΔT | Per nameplate |  | °F | Per nameplate
© Your HVAC Co. ¦ Rogers, AR ¦ (555) 867-5309 ¦ www.yourhvac.com

## Component Condition Ratings
Your HVAC Co. |  |  |  | RTU COMPONENT CONDITION RATINGS & RECOMMENDATIONS
Rogers, AR • (555) 867-5309 • www.yourhvac.com • service@yourhvac.com
📊 CONDITION RATING LEGEND
G = Good (no action) F = Fair (monitor / note) P = Poor (recommend replacement) N/A = Not applicable
🏗️ ROOFTOP STRUCTURAL & MOUNTING
# | Component | Good | Fair | Poor | N/A | Action Required / Notes
1 | Unit Curb / Rails | ☐ G | ☐ F | ☐ P | ☐ N/A
2 | Curb-to-Deck Fasteners | ☐ G | ☐ F | ☐ P | ☐ N/A
3 | Roof Membrane Around Curb | ☐ G | ☐ F | ☐ P | ☐ N/A
4 | Curb Gasket / Seal | ☐ G | ☐ F | ☐ P | ☐ N/A
5 | Vibration Isolators | ☐ G | ☐ F | ☐ P | ☐ N/A
6 | Flexible Duct Connectors | ☐ G | ☐ F | ☐ P | ☐ N/A
7 | Refrigerant Line Insulation (roof) | ☐ G | ☐ F | ☐ P | ☐ N/A
8 | Condensate Piping (roof) | ☐ G | ☐ F | ☐ P | ☐ N/A
9 | Electrical Conduit / Weatherheads | ☐ G | ☐ F | ☐ P | ☐ N/A
10 | Bird / Pest Screening | ☐ G | ☐ F | ☐ P | ☐ N/A
🌀 AIRSIDE & FILTRATION COMPONENTS
# | Component | Good | Fair | Poor | N/A | Action Required / Notes
1 | Air Filters | ☐ G | ☐ F | ☐ P | ☐ N/A
2 | Filter Rack / Bypass Seals | ☐ G | ☐ F | ☐ P | ☐ N/A
3 | Blower Wheel | ☐ G | ☐ F | ☐ P | ☐ N/A
4 | Blower Motor | ☐ G | ☐ F | ☐ P | ☐ N/A
5 | Blower Motor Capacitor | ☐ G | ☐ F | ☐ P | ☐ N/A
6 | Drive Belt(s) | ☐ G | ☐ F | ☐ P | ☐ N/A
7 | Drive Sheaves / Pulleys | ☐ G | ☐ F | ☐ P | ☐ N/A
8 | VFD (if installed) | ☐ G | ☐ F | ☐ P | ☐ N/A
9 | Economizer Damper Blades (OA) | ☐ G | ☐ F | ☐ P | ☐ N/A
10 | Economizer Damper Blades (RA/Exhaust) | ☐ G | ☐ F | ☐ P | ☐ N/A
11 | Economizer Actuator(s) | ☐ G | ☐ F | ☐ P | ☐ N/A
12 | Economizer Sensor / Controller | ☐ G | ☐ F | ☐ P | ☐ N/A
13 | OA Intake Hood / Screen | ☐ G | ☐ F | ☐ P | ☐ N/A
14 | Evaporator Coil | ☐ G | ☐ F | ☐ P | ☐ N/A
15 | Evaporator Coil Fins | ☐ G | ☐ F | ☐ P | ☐ N/A
16 | Drain Pan | ☐ G | ☐ F | ☐ P | ☐ N/A
17 | Condensate Drain / Trap | ☐ G | ☐ F | ☐ P | ☐ N/A
18 | Condensate Overflow Sensor | ☐ G | ☐ F | ☐ P | ☐ N/A
❄️ REFRIGERANT & CONDENSER COMPONENTS
# | Component | Good | Fair | Poor | N/A | Action Required / Notes
1 | Condenser Coil — Circuit 1 | ☐ G | ☐ F | ☐ P | ☐ N/A
2 | Condenser Coil — Circuit 2 (if appl.) | ☐ G | ☐ F | ☐ P | ☐ N/A
3 | Condenser Coil Fins | ☐ G | ☐ F | ☐ P | ☐ N/A
4 | Condenser Fan Blades (all) | ☐ G | ☐ F | ☐ P | ☐ N/A
5 | Condenser Fan Motors (all) | ☐ G | ☐ F | ☐ P | ☐ N/A
6 | Condenser Fan Capacitors | ☐ G | ☐ F | ☐ P | ☐ N/A
7 | Compressor — Circuit 1 | ☐ G | ☐ F | ☐ P | ☐ N/A
8 | Compressor — Circuit 2 (if appl.) | ☐ G | ☐ F | ☐ P | ☐ N/A
9 | Compressor Run Capacitor(s) | ☐ G | ☐ F | ☐ P | ☐ N/A
10 | Start Cap / Hard-Start Kit | ☐ G | ☐ F | ☐ P | ☐ N/A
11 | Crankcase Heater(s) | ☐ G | ☐ F | ☐ P | ☐ N/A
12 | Service Valves | ☐ G | ☐ F | ☐ P | ☐ N/A
13 | Filter Dryer(s) | ☐ G | ☐ F | ☐ P | ☐ N/A
14 | Sight Glass(es) | ☐ G | ☐ F | ☐ P | ☐ N/A
15 | TXV / EEV Metering Device(s) | ☐ G | ☐ F | ☐ P | ☐ N/A
16 | Refrigerant Lines & Insulation | ☐ G | ☐ F | ☐ P | ☐ N/A
17 | Contactor(s) | ☐ G | ☐ F | ☐ P | ☐ N/A
18 | Disconnect Box(es) | ☐ G | ☐ F | ☐ P | ☐ N/A
🔥 GAS HEAT & ELECTRICAL COMPONENTS
# | Component | Good | Fair | Poor | N/A | Action Required / Notes
1 | Gas Burners | ☐ G | ☐ F | ☐ P | ☐ N/A
2 | Ignitor | ☐ G | ☐ F | ☐ P | ☐ N/A
3 | Flame Sensor | ☐ G | ☐ F | ☐ P | ☐ N/A
4 | Heat Exchanger (visual) | ☐ G | ☐ F | ☐ P | ☐ N/A
5 | Inducer Motor | ☐ G | ☐ F | ☐ P | ☐ N/A
6 | Inducer Wheel | ☐ G | ☐ F | ☐ P | ☐ N/A
7 | Flue / Exhaust Vent Connection | ☐ G | ☐ F | ☐ P | ☐ N/A
8 | Flue Rain Cap / Hood | ☐ G | ☐ F | ☐ P | ☐ N/A
9 | Pressure Switch Hoses | ☐ G | ☐ F | ☐ P | ☐ N/A
10 | Gas Valve | ☐ G | ☐ F | ☐ P | ☐ N/A
11 | Rollout Switch | ☐ G | ☐ F | ☐ P | ☐ N/A
12 | High-Limit Switch | ☐ G | ☐ F | ☐ P | ☐ N/A
13 | Control Board(s) | ☐ G | ☐ F | ☐ P | ☐ N/A
14 | Low-Voltage Wiring / Terminals | ☐ G | ☐ F | ☐ P | ☐ N/A
15 | Main Power Wiring / Conduit | ☐ G | ☐ F | ☐ P | ☐ N/A
16 | BAS / DDC Controller | ☐ G | ☐ F | ☐ P | ☐ N/A
© Your HVAC Co. ¦ Rogers, AR ¦ (555) 867-5309 ¦ www.yourhvac.com

## Service Summary & Closeout
Your HVAC Co. |  |  |  | SERVICE SUMMARY, RECOMMENDATIONS & PM CLOSEOUT
Rogers, AR • (555) 867-5309 • www.yourhvac.com • service@yourhvac.com
🔧 SECTION A — PARTS & MATERIALS USED THIS SERVICE
# | Part Number | Description | Qty | Unit Cost | Total Cost | Notes
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
📋 SECTION B — SERVICE RECOMMENDATIONS & FINDINGS
# | Date | Recommendation / Finding | Priority | Est. Cost | Quoted | Accepted
1 |  |  | High
2 |  |  | High
3 |  |  | High
4 |  |  | Medium
5 |  |  | Medium
6 |  |  | Medium
7 |  |  | Medium
8 |  |  | Low
9 |  |  | Low
10 |  |  | Low
11 |  |  | Low
12 |  |  | Low
✅ SECTION C — PM CLOSEOUT VERIFICATION
Rooftop safety procedures followed throughout service? (Y/N):
All PM checklist sections completed? (Y/N):
All measured data recorded and within specification? (Y/N):
Refrigerant leak check performed — all circuits passed? (Y/N):
Filters replaced — size, MERV, and quantity logged? (Y/N):
All panels, access doors, and fasteners reinstalled? (Y/N):
All fault codes cleared — unit operating normally at departure? (Y/N):
BAS / DDC trends and alarms verified before leaving? (Y/N):
Economizer operation verified in free-cooling and lockout modes? (Y/N):
Roof surface clean — no tools, debris, or rags left behind? (Y/N):
Customer / FM notified of completion and informed of findings? (Y/N):
All recommendations quoted and provided in writing? (Y/N):
Service report copy provided to customer / FM? (Y/N):
PM report and photos uploaded to company system? (Y/N):
Next PM date confirmed and scheduled? (Y/N):
📝 SECTION D — TECHNICIAN NOTES & ADDITIONAL OBSERVATIONS
Technician notes / additional observations:
🖊️ SECTION E — PM SERVICE SIGN-OFF SIGNATURES
Lead Technician Signature:
Print Name: |  | Date: |  | License / EPA Cert #:
Assisting Technician (if applicable):
Print Name: |  | Date: |  | License / Cert #:
Customer / Facility Manager Signature:
Print Name: |  | Date: |  | Title:
© Your HVAC Co. ¦ Rogers, AR ¦ (555) 867-5309 ¦ www.yourhvac.com