HVAC PREVENTIVE MAINTENANCE AGREEMENT This Agreement is entered into by and between the parties identified below.

📋  SECTION 1 — PARTIES & AGREEMENT IDENTIFICATION

| SERVICE PROVIDER (CONTRACTOR) | CLIENT (CUSTOMER) |
| --- | --- |
| Company Name: ________________________ | Client/Company Name: ________________________ |
| DBA (if applicable): ________________________ | Contact Name: ________________________ |
| Contractor License #: ________________________ | Title/Role: ________________________ |
| Address: ________________________ | Service Address: ________________________ |
| City, State, ZIP: ________________________ | City, State, ZIP: ________________________ |
| Phone: ________________________ | Phone: ________________________ |
| Email: ________________________ | Email: ________________________ |
| EPA 608 Cert #: ________________________ | Billing Address (if different): ________________________ |

| Agreement # | Effective Date | Expiration Date | Service Plan |
| --- | --- | --- | --- |
| ___________ | ___________ | ___________ | ___________ |

🔧  SECTION 2 — SCOPE OF PREVENTIVE MAINTENANCE SERVICES

The Contractor agrees to perform the following scheduled preventive maintenance (PM) services on the equipment identified in Section 3 (Equipment Schedule). All services shall be performed by certified technicians in accordance with manufacturer recommendations, ASHRAE standards, and applicable code.

| Service Plan | Annual Visit Frequency |
| --- | --- |
| Bronze | 1 Visit/Year |
| Silver | 2 Visits/Year |
| Gold | 4 Visits/Year |
| Platinum | 12 Visits/Year (Monthly) |

2.1  COOLING SYSTEM SERVICES (Performed at Each Visit)

| Cooling System Task | Pass | Fail | N/A |
| --- | --- | --- | --- |
| Inspect and clean condenser coils | ☐ | ☐ | ☐ |
| Inspect and clean evaporator coils | ☐ | ☐ | ☐ |
| Check and record refrigerant pressures (suction / discharge) | ☐ | ☐ | ☐ |
| Check refrigerant charge — add if deficient (billed separately) | ☐ | ☐ | ☐ |
| Inspect compressor operation and amp draw | ☐ | ☐ | ☐ |
| Lubricate condenser fan motor bearings | ☐ | ☐ | ☐ |
| Inspect fan blades for damage/balance | ☐ | ☐ | ☐ |
| Check condenser fan motor contactor and capacitors | ☐ | ☐ | ☐ |
| Inspect economizer (if equipped) — dampers, actuators, sensors | ☐ | ☐ | ☐ |
| Verify thermostat setpoints and operation | ☐ | ☐ | ☐ |
| Clean condensate drain pan and test drain lines | ☐ | ☐ | ☐ |
| Inspect and replace air filters (standard 1" — non-standard billed separately) | ☐ | ☐ | ☐ |
| Check electrical connections and torque as needed | ☐ | ☐ | ☐ |
| Record supply and return air temperatures | ☐ | ☐ | ☐ |

2.2  HEATING SYSTEM SERVICES (Performed at Each Visit)

| Heating System Task | Pass | Fail | N/A |
| --- | --- | --- | --- |
| Inspect heat exchanger for cracks or corrosion (gas furnace) | ☐ | ☐ | ☐ |
| Clean burners and inspect igniter / flame sensor | ☐ | ☐ | ☐ |
| Test gas pressure — manifold and supply | ☐ | ☐ | ☐ |
| Inspect flue and venting for obstructions or deterioration | ☐ | ☐ | ☐ |
| Check safety controls — high-limit, pressure switches | ☐ | ☐ | ☐ |
| Test heating sequence of operation | ☐ | ☐ | ☐ |
| Inspect and test heat pump reversing valve (heat pump systems) | ☐ | ☐ | ☐ |
| Check auxiliary / emergency heat strips — amp draw | ☐ | ☐ | ☐ |
| Inspect humidifier (if equipped) — pads, float, water supply | ☐ | ☐ | ☐ |
| Verify thermostat heating setpoints and staging | ☐ | ☐ | ☐ |
| Check and clean heat exchanger secondary if applicable | ☐ | ☐ | ☐ |

2.3  ELECTRICAL & CONTROLS

| Electrical / Controls Task | Pass | Fail | N/A |
| --- | --- | --- | --- |
| Inspect and tighten all electrical connections | ☐ | ☐ | ☐ |
| Check contactors — inspect contacts for pitting or burning | ☐ | ☐ | ☐ |
| Test start and run capacitors | ☐ | ☐ | ☐ |
| Measure and record motor amperage (all motors) | ☐ | ☐ | ☐ |
| Test transformer output voltage | ☐ | ☐ | ☐ |
| Inspect control board for fault codes or burn marks | ☐ | ☐ | ☐ |
| Test defrost controls and board (heat pump) | ☐ | ☐ | ☐ |
| Verify economizer controls and sensors (DDC / analog) | ☐ | ☐ | ☐ |
| Check VFD drives — fault history, parameter check (if equipped) | ☐ | ☐ | ☐ |

⚙️  SECTION 3 — EXHIBIT A: EQUIPMENT SCHEDULE

All equipment covered under this Agreement is identified below. Additional equipment may be added via Change Order (Exhibit D).

| # | Equipment Type | Make / Model | Serial # | Location | Tonnage/MBH | Install Year | Notes |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |  |
| 6 |  |  |  |  |  |  |  |

📊  SECTION 4 — FIELD MEASUREMENT & PERFORMANCE DATA

Complete this section during each service visit. Record measured values for each unit inspected.

| Parameter | Unit # | Measured | Unit | Spec / Range | Status | Notes |
| --- | --- | --- | --- | --- | --- | --- |
| Supply Air Temp |  |  | °F | 50–58°F (clg) |  |  |
| Return Air Temp |  |  | °F |  |  |  |
| Delta T (ΔT) |  |  | °F | 16–22°F typical |  |  |
| Suction Pressure |  |  | psig | Per refrigerant |  |  |
| Discharge Pressure |  |  | psig | Per refrigerant |  |  |
| Superheat |  |  | °F | 10–20°F |  |  |
| Subcooling |  |  | °F | 10–15°F |  |  |
| Compressor Amps |  |  | A | Per nameplate |  |  |
| Condenser Fan Amps |  |  | A | Per nameplate |  |  |
| Blower Motor Amps |  |  | A | Per nameplate |  |  |
| Gas Manifold Pressure |  |  | "W.C. | 3.5" nat / 10" LP |  |  |
| Flue Temp |  |  | °F |  |  |  |
| CO in Flue |  |  | ppm | < 400 ppm |  |  |

💰  SECTION 5 — CONTRACT PRICING & PAYMENT TERMS

| Description | Unit Price | Qty | Frequency | Total |
| --- | --- | --- | --- | --- |
| Annual PM Agreement — Base | $________ | 1 | Annual | $________ |
| Additional Equipment Units | $________ | ___ | Annual | $________ |
| Filter Replacement (non-standard) | $________ | ___ | Per visit | $________ |
| Refrigerant (if required) | $________ | ___ | Per lb | $________ |
| Optional Add-on: Belt/Bearing Kit | $________ | 1 | Annual | $________ |
| TOTAL ANNUAL CONTRACT PRICE: |  |  |  | $________ |

5.1  PAYMENT TERMS

5.1.1  Payment is due within [30] days of invoice date unless otherwise specified in writing.

5.1.2  Annual contracts may be paid in full or in equal quarterly installments (if agreed in writing).

5.1.3  Invoices not paid within 30 days are subject to a late charge of 1.5% per month (18% per annum).

5.1.4  Materials, refrigerant, and non-standard repairs not included in the base price will be invoiced separately.

5.1.5  Contractor reserves the right to suspend service for non-payment after [15] days past due.

🚨  SECTION 6 — EMERGENCY & ON-CALL SERVICE

| Service Type | Rate | Coverage Hours |
| --- | --- | --- |
| Standard Labor Rate | $______/hr | Mon–Fri 7AM–5PM |
| After-Hours Emergency Rate | $______/hr | Mon–Fri 5PM–7AM |
| Weekend / Holiday Rate | $______/hr | Sat, Sun, Holidays |
| Trip Charge (Emergency) | $______/call | After-Hours only |
| Emergency Response Time | _______ hours | Best effort |

6.1.1  Emergency service requests must be placed via the Contractor's designated service dispatch line.

6.1.2  Emergency labor and materials are billed at rates above and are not included in the base contract price.

6.1.3  Contract holders receive priority scheduling over non-contract accounts.

🏢  SECTION 7 — CLIENT RESPONSIBILITIES

7.1  Client shall provide safe and unobstructed access to all equipment covered under this Agreement during scheduled service visits.

7.2  Client shall notify Contractor of any known equipment deficiencies, prior damage, or tenant complaints prior to scheduled visits.

7.3  Client shall maintain building temperatures and humidity within normal operating ranges between service visits.

7.4  Client shall not alter, repair, or permit any third party to service equipment covered under this Agreement without prior written notice to Contractor.

7.5  Client shall provide a designated contact person with authority to approve repairs or additional work discovered during visits.

7.6  Client shall ensure all equipment is energized and in serviceable condition at time of scheduled visit. Re-dispatch fees apply if equipment is inaccessible.

🛡️  SECTION 8 — WARRANTIES, LIABILITY & INDEMNIFICATION

8.1  Contractor warrants that all PM services will be performed in a professional and workmanlike manner consistent with industry standards.

8.2  Contractor does not warrant against equipment failure caused by age, pre-existing conditions, deferred maintenance, power surges, or events outside Contractor's control.

8.3  Contractor's liability under this Agreement shall not exceed the total contract price paid in the prior 12-month period.

8.4  In no event shall Contractor be liable for consequential, incidental, or punitive damages including lost profits, spoilage, data loss, or business interruption.

8.5  Each party shall indemnify and hold harmless the other party from claims arising from the indemnifying party's own negligence or willful misconduct.

8.6  Contractor shall maintain Commercial General Liability (min. $1,000,000 per occurrence), Workers' Compensation, and Auto Liability insurance throughout the term.

🧪  SECTION 9 — REFRIGERANT MANAGEMENT & REGULATORY COMPLIANCE

9.1  All refrigerant work performed under this Agreement shall be conducted by EPA Section 608-certified technicians in accordance with 40 CFR Part 82.

9.2  Contractor shall maintain refrigerant addition records for all equipment with a charge of 50 lbs or more as required under EPA leak repair regulations.

9.3  Systems with leak rates exceeding EPA thresholds shall be reported to Client in writing with recommended corrective action.

9.4  Refrigerant recovered during service shall be handled, recycled, or reclaimed in accordance with all applicable federal, state, and local regulations.

9.5  Client shall not vent refrigerant or engage any uncertified personnel to work on refrigerant-containing systems.

📅  SECTION 10 — TERM, RENEWAL & TERMINATION

10.1  This Agreement commences on the Effective Date and continues for a period of one (1) year unless otherwise specified.

10.2  This Agreement shall automatically renew for successive one-year terms unless either party provides written notice of non-renewal at least [30] days before expiration.

10.3  Either party may terminate this Agreement with [30] days written notice. Client shall be responsible for the pro-rated contract amount through the date of termination.

10.4  Contractor may terminate immediately upon non-payment of invoices outstanding for more than [60] days.

10.5  Annual pricing is subject to review upon each renewal. Contractor shall provide notice of any price adjustment no less than [30] days prior to renewal date.

⚖️  SECTION 11 — GENERAL PROVISIONS

11.1 ENTIRE AGREEMENT  This Agreement, together with all attached Exhibits, constitutes the entire agreement between the parties and supersedes all prior negotiations, representations, or agreements.

11.2 AMENDMENTS  This Agreement may not be modified except by written amendment signed by both parties.

11.3 GOVERNING LAW  This Agreement shall be governed by the laws of the State of ________________.

11.4 DISPUTE RESOLUTION  Disputes shall first be submitted to good-faith mediation. If mediation fails, disputes shall be resolved by binding arbitration per the rules of the American Arbitration Association.

11.5 FORCE MAJEURE  Neither party shall be in default for failure to perform caused by events beyond reasonable control, including natural disasters, pandemics, or government orders.

11.6 SUBCONTRACTING  Contractor may subcontract portions of this work to qualified, licensed sub-contractors. Contractor remains responsible for subcontracted work.

11.7 SEVERABILITY  If any provision is found invalid, the remaining provisions shall continue in full force and effect.

11.8 NOTICES  All notices shall be in writing and delivered by certified mail, email with read receipt, or hand delivery to the addresses in Section 1.

📝  SECTION 12 — SPECIAL CONDITIONS & ADDENDA

The following special conditions, modifications, or addenda are incorporated into and made part of this Agreement:

1. ____________________________________________________________________________________________

2. ____________________________________________________________________________________________

3. ____________________________________________________________________________________________

4. ____________________________________________________________________________________________

5. ____________________________________________________________________________________________

Exhibits Incorporated by Reference:  Exhibit A — PM Checklist  |  Exhibit B — Equipment Schedule  |  Exhibit C — Pricing Schedule  |  Exhibit D — Change Order Form

✍️  SECTION 13 — EXECUTION & AUTHORIZATION

THE PARTIES HEREBY AGREE to all terms and conditions set forth in this Agreement, including all Exhibits attached hereto. Each signatory represents that they are authorized to bind their respective party.

| SERVICE PROVIDER (CONTRACTOR) | CLIENT (CUSTOMER) |
| --- | --- |
| Authorized Signature: ____________________________ | Authorized Signature: ____________________________ |
| Printed Name: ____________________________ | Printed Name: ____________________________ |
| Title: ____________________________ | Title: ____________________________ |
| Date: ____________________________ | Date: ____________________________ |
| Company Name: ____________________________ | Company Name: ____________________________ |

This document is a template for use by qualified HVAC contractors. Consult a licensed attorney before use. [Your HVAC Co.] makes no warranty as to the legal sufficiency of this template in any jurisdiction.