HVAC SYSTEM INSPECTION CHECKLIST Complete all applicable sections. Mark Pass / Fail / N/A. Record all measurements and observations.

📋  SECTION 1 — JOB & TECHNICIAN INFORMATION

| Work Order #: ________________________ | Inspection Date: ________________________ |
| --- | --- |
| Technician Name: ________________________ | Technician ID / Cert #: ________________________ |
| Customer Name: ________________________ | Phone: ________________________ |
| Service Address: ________________________ | City / State / ZIP: ________________________ |
| Inspection Type: ☐ Preventive ☐ Diagnostic ☐ Pre-Season ☐ Post-Repair | Season: ☐ Spring/Cooling ☐ Fall/Heating |
| Contract / Agreement #: ________________________ | Invoice # (if applicable): ________________________ |

🏠  SECTION 2 — SYSTEM IDENTIFICATION

| System Type: ☐ Split ☐ Package ☐ Mini-Split ☐ VRF ☐ Chiller | Application: ☐ Residential ☐ Light Comm. ☐ Commercial |
| --- | --- |
| Equipment Brand: ________________________ | AHU / Air Handler Model #: ________________________ |
| Outdoor Unit Model #: ________________________ | Serial #: ________________________ |
| Equipment Install Date: ________________________ | System Age: ____________ years |
| Refrigerant Type: ☐ R-22 ☐ R-410A ☐ R-454B ☐ R-32 ☐ Other: | System Tonnage / Capacity: ____________ tons / BTU |
| Location – AHU: ________________________ | Location – Condenser: ________________________ |
| Thermostat Brand/Model: ________________________ | Control Type: ☐ Manual ☐ Programmable ☐ Smart/WiFi |

⚡  SECTION 3 — ELECTRICAL INSPECTION

Voltage & Amperage Readings

| Parameter / Item | Measured | Unit | Spec / Range | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| Power Supply |  |  |  |  |  |
| Supply Voltage (L1–L2) |  | VAC | ±10% of nameplate | ☐ OK ☐ Fail |  |
| Supply Voltage (L1–N) |  | VAC | 120V nominal | ☐ OK ☐ Fail |  |
| Supply Voltage (L2–N) |  | VAC | 120V nominal | ☐ OK ☐ Fail |  |
| Compressor |  |  |  |  |  |
| Compressor RLA (Running) |  | A | ≤ nameplate RLA | ☐ OK ☐ Fail |  |
| Compressor LRA (Locked Rotor) |  | A | Per nameplate | ☐ OK ☐ Fail |  |
| Motors |  |  |  |  |  |
| Condenser Fan Motor Amps |  | A | ≤ nameplate FLA | ☐ OK ☐ Fail |  |
| Blower / AHU Motor Amps |  | A | ≤ nameplate FLA | ☐ OK ☐ Fail |  |
| Control Circuit |  |  |  |  |  |
| 24V Control Voltage |  | VAC | 24–28 VAC | ☐ OK ☐ Fail |  |

Electrical Components

| Component / Check Item | Pass | Fail | N/A | Notes / Reading |
| --- | --- | --- | --- | --- |
| Disconnect – proper size, accessible, clear of debris | ☐ | ☐ | ☐ |  |
| Fuses / breakers – correct amp rating, not blown/tripped | ☐ | ☐ | ☐ |  |
| Contactor – contacts not pitted or burned, coil OK | ☐ | ☐ | ☐ |  |
| Capacitor – start & run (no bulging, correct µF rating) | ☐ | ☐ | ☐ |  |
| Wiring – no exposed conductors, tight connections, no corrosion | ☐ | ☐ | ☐ |  |
| Control board – no burn marks, secure mounting, LEDs normal | ☐ | ☐ | ☐ |  |
| Ground wires – present, secure, continuity OK | ☐ | ☐ | ☐ |  |
| Thermostat wiring – labeled, secure, no bare conductors | ☐ | ☐ | ☐ |  |

❄️  SECTION 4 — REFRIGERATION SYSTEM

Refrigerant Pressures & Temperatures

| Parameter / Item | Measured | Unit | Spec / Range | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| Cooling Mode |  |  |  |  |  |
| Suction Pressure |  | PSIG | Per mfr. chart | ☐ OK ☐ Fail |  |
| Discharge Pressure |  | PSIG | Per mfr. chart | ☐ OK ☐ Fail |  |
| Suction Line Temp (at service valve) |  | °F | Per mfr. chart | ☐ OK ☐ Fail |  |
| Liquid Line Temp |  | °F | Per mfr. chart | ☐ OK ☐ Fail |  |
| Evaporator Saturation Temp |  | °F | Calc. from suction | ☐ OK ☐ Fail |  |
| Condenser Saturation Temp |  | °F | Calc. from discharge | ☐ OK ☐ Fail |  |
| Superheat / Subcooling |  |  |  |  |  |
| Actual Superheat |  | °F | Per mfr. target | ☐ OK ☐ Fail |  |
| Target Superheat |  | °F | Per chart | — |  |
| Actual Subcooling |  | °F | Per mfr. target | ☐ OK ☐ Fail |  |
| Target Subcooling |  | °F | Per chart | — |  |

Refrigerant System Components

| Component / Check Item | Pass | Fail | N/A | Notes / Reading |
| --- | --- | --- | --- | --- |
| Refrigerant charge – correct per superheat/subcooling method | ☐ | ☐ | ☐ |  |
| Leak check – no visible oil staining, electronic/UV dye test OK | ☐ | ☐ | ☐ |  |
| TXV / Metering device – operating correctly, bulb secure | ☐ | ☐ | ☐ |  |
| Filter drier – within service interval, no excessive pressure drop | ☐ | ☐ | ☐ |  |
| Sight glass – clear, no bubbles (liquid line, if equipped) | ☐ | ☐ | ☐ |  |
| Reversing valve – operates correctly in both modes (heat pump) | ☐ | ☐ | ☐ |  |
| Defrost board / sensors – tested, initiates and terminates properly | ☐ | ☐ | ☐ |  |
| Refrigerant log updated – quantity added (oz): ____________ | ☐ | ☐ | ☐ |  |

💨  SECTION 5 — AIR HANDLER / FURNACE INSPECTION

Airflow Measurements

| Parameter / Item | Measured | Unit | Spec / Range | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| Supply Air Temp (SA) |  | °F | Per system design | ☐ OK ☐ Fail |  |
| Return Air Temp (RA) |  | °F | Per system design | ☐ OK ☐ Fail |  |
| Temperature Differential (ΔT) |  | °F | 16–22°F cooling | ☐ OK ☐ Fail |  |
| Static Pressure – Supply |  | in. w.c. | Per design | ☐ OK ☐ Fail |  |
| Static Pressure – Return |  | in. w.c. | Per design | ☐ OK ☐ Fail |  |
| Total External Static Pressure |  | in. w.c. | ≤ nameplate max | ☐ OK ☐ Fail |  |
| Estimated CFM |  | CFM | Per system sizing | ☐ OK ☐ Fail |  |

Air Handler Components

| Component / Check Item | Pass | Fail | N/A | Notes / Reading |
| --- | --- | --- | --- | --- |
| Filter & Coil |  |  |  |  |
| Air filter – condition checked, replaced if needed (size: ____________) | ☐ | ☐ | ☐ |  |
| Evaporator coil – clean, no ice, no corrosion, no debris | ☐ | ☐ | ☐ |  |
| Drain pan – clean, no standing water, no algae/slime | ☐ | ☐ | ☐ |  |
| Condensate drain line – clear, flow tested, trap primed | ☐ | ☐ | ☐ |  |
| Condensate pump – operational, overflow switch tested | ☐ | ☐ | ☐ |  |
| Blower Assembly |  |  |  |  |
| Blower wheel – clean, no debris buildup, no wobble | ☐ | ☐ | ☐ |  |
| Blower motor – lubricated (if required), no noise, correct rotation | ☐ | ☐ | ☐ |  |
| Blower belt – tension OK, no cracks or fraying (if belt-drive) | ☐ | ☐ | ☐ |  |
| Blower housing – clean, no leaks, tight connections | ☐ | ☐ | ☐ |  |
| Heat Section (Furnace / Heat Strip) |  |  |  |  |
| Heat exchanger – no cracks, corrosion, or holes (furnace) | ☐ | ☐ | ☐ |  |
| Burners – clean, flame pattern correct (blue, no yellow tips) | ☐ | ☐ | ☐ |  |
| Igniter / pilot – operational, no cracks (if applicable) | ☐ | ☐ | ☐ |  |
| Heat strips – correct kW, no open elements, sequencers OK | ☐ | ☐ | ☐ |  |
| Flue / vent pipe – secure, no blockage, no backdraft | ☐ | ☐ | ☐ |  |
| Gas pressure – manifold pressure correct per nameplate | ☐ | ☐ | ☐ |  |
| Gas valve – opens/closes properly, no leaks (gas soap test) | ☐ | ☐ | ☐ |  |
| Limit switch – reset, no evidence of nuisance tripping | ☐ | ☐ | ☐ |  |

🌀  SECTION 6 — CONDENSER / OUTDOOR UNIT INSPECTION

| Component / Check Item | Pass | Fail | N/A | Notes / Reading |
| --- | --- | --- | --- | --- |
| Mechanical |  |  |  |  |
| Condenser coil – clean, fins straight, no debris blocking airflow | ☐ | ☐ | ☐ |  |
| Condenser fan blade – no cracks, correct pitch, tight on shaft | ☐ | ☐ | ☐ |  |
| Condenser fan motor – correct rotation, no noise, secure mounting | ☐ | ☐ | ☐ |  |
| Compressor – no abnormal noise, no oil staining on body | ☐ | ☐ | ☐ |  |
| Compressor crankcase heater – operational (if equipped) | ☐ | ☐ | ☐ |  |
| Structural & Clearances |  |  |  |  |
| Unit level – pad/roof curb level within 1/4" | ☐ | ☐ | ☐ |  |
| Service clearances – 12" minimum on all sides / per mfr. | ☐ | ☐ | ☐ |  |
| Refrigerant lines – insulation intact, properly supported, no kinks | ☐ | ☐ | ☐ |  |
| Electrical conduit – secure, no cracks, no exposed wiring | ☐ | ☐ | ☐ |  |
| Unit housing – panels secured, no damage, no sharp edges | ☐ | ☐ | ☐ |  |
| Vegetation / debris clearance – 18" minimum around unit | ☐ | ☐ | ☐ |  |

🌡️  SECTION 7 — THERMOSTAT & CONTROLS

| Component / Check Item | Pass | Fail | N/A | Notes / Reading |
| --- | --- | --- | --- | --- |
| Thermostat – level, secure, correct temperature reading | ☐ | ☐ | ☐ |  |
| Cool mode – calls cooling, compressor and fan energize correctly | ☐ | ☐ | ☐ |  |
| Heat mode – calls heating, correct sequence of operation | ☐ | ☐ | ☐ |  |
| Fan mode – auto/on modes functional | ☐ | ☐ | ☐ |  |
| Temperature setpoints – programming verified with customer | ☐ | ☐ | ☐ |  |
| Thermostat batteries – replaced if needed | ☐ | ☐ | ☐ |  |
| Zoning controls – all zones tested, dampers operate correctly | ☐ | ☐ | ☐ |  |
| BAS / BMS integration – points verified (commercial, if applicable) | ☐ | ☐ | ☐ |  |
| Emergency heat – tested and operational (heat pump) | ☐ | ☐ | ☐ |  |
| Humidistat / dehumidistat – setpoints verified (if equipped) | ☐ | ☐ | ☐ |  |
| IAQ controls (UV, ionizer, ERV/HRV) – operational status verified | ☐ | ☐ | ☐ |  |

🌬️  SECTION 8 — INDOOR AIR QUALITY & SAFETY

IAQ Measurements

| Parameter / Item | Measured | Unit | Spec / Range | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| Return Air Dry Bulb |  | °F | Per setpoint | ☐ OK ☐ N/A |  |
| Return Air Wet Bulb |  | °F | Per setpoint | ☐ OK ☐ N/A |  |
| Indoor Relative Humidity |  | %RH | 40–60% RH | ☐ OK ☐ N/A |  |
| CO Level (ambient) |  | ppm | < 9 ppm (ASHRAE) | ☐ OK ☐ N/A |  |
| CO₂ Level (occupied) |  | ppm | < 1100 ppm | ☐ OK ☐ N/A |  |

IAQ Components & Safety Devices

| Component / Check Item | Pass | Fail | N/A | Notes / Reading |
| --- | --- | --- | --- | --- |
| CO / gas detector – tested, in date, within 5 ft of appliance | ☐ | ☐ | ☐ |  |
| Smoke detector (AHU area) – tested | ☐ | ☐ | ☐ |  |
| UV lamp(s) – operational, within replacement interval | ☐ | ☐ | ☐ |  |
| Electronic air cleaner – cells cleaned, ionizer wires intact | ☐ | ☐ | ☐ |  |
| Media filter / HEPA – condition OK, within change interval | ☐ | ☐ | ☐ |  |
| ERV / HRV – core clean, balanced, dampers operational | ☐ | ☐ | ☐ |  |
| Humidifier – pad/drum inspected, water panel replaced if needed | ☐ | ☐ | ☐ |  |
| Dehumidifier – drain clear, operational | ☐ | ☐ | ☐ |  |
| Odors – no unusual odors (mold, gas, burning) noted | ☐ | ☐ | ☐ |  |

📐  SECTION 9 — DUCT SYSTEM INSPECTION

| Component / Check Item | Pass | Fail | N/A | Notes / Reading |
| --- | --- | --- | --- | --- |
| Supply System |  |  |  |  |
| Supply ducts – no visible damage, disconnects, or leaks | ☐ | ☐ | ☐ |  |
| Supply registers – clean, open, correctly balanced | ☐ | ☐ | ☐ |  |
| Supply plenum – insulated, sealed at AHU connection | ☐ | ☐ | ☐ |  |
| Return System |  |  |  |  |
| Return grilles – clean, not blocked by furniture/drapes | ☐ | ☐ | ☐ |  |
| Return ducts – no disconnects, no unintentional air paths | ☐ | ☐ | ☐ |  |
| Return air pathway – adequate area per system CFM | ☐ | ☐ | ☐ |  |
| General |  |  |  |  |
| Duct insulation – intact, R-value appropriate for location | ☐ | ☐ | ☐ |  |
| Flexible duct – not kinked, not excessively compressed | ☐ | ☐ | ☐ |  |
| Duct support – hangers within 4 ft, no sagging | ☐ | ☐ | ☐ |  |
| Air balance – spot-check with magnehelic or flow hood | ☐ | ☐ | ☐ |  |

📝  SECTION 10 — FINDINGS, RECOMMENDATIONS & PARTS

Items Requiring Immediate Attention

| # | Description of Finding | Recommended Action | Priority |
| --- | --- | --- | --- |
| 1 |  | ☐ Repair ☐ Replace ☐ Monitor | ☐ Urgent ☐ Routine |
| 2 |  | ☐ Repair ☐ Replace ☐ Monitor | ☐ Urgent ☐ Routine |
| 3 |  | ☐ Repair ☐ Replace ☐ Monitor | ☐ Urgent ☐ Routine |
| 4 |  | ☐ Repair ☐ Replace ☐ Monitor | ☐ Urgent ☐ Routine |
| 5 |  | ☐ Repair ☐ Replace ☐ Monitor | ☐ Urgent ☐ Routine |

Parts / Materials Used or Recommended

| Part / Material Description | Part # | Qty Used | Qty Needed | Status |
| --- | --- | --- | --- | --- |
|  |  |  |  | ☐ Installed ☐ On Order |
|  |  |  |  | ☐ Installed ☐ On Order |
|  |  |  |  | ☐ Installed ☐ On Order |
|  |  |  |  | ☐ Installed ☐ On Order |

General Notes / Observations

✅  SECTION 11 — OVERALL SYSTEM STATUS

Overall System Condition: ☐ Excellent ☐ Good ☐ Fair ☐ Poor ☐ Unsafe – Do Not Operate

System Operational at Completion: ☐ Yes – fully operational ☐ No – pending parts/repair ☐ Partial

Follow-Up Visit Required: ☐ Yes ☐ No If Yes, scheduled for: ________________________

Customer Informed of Findings: ☐ Yes ☐ No Verbal ☐ Written ☐

Additional Quote Required: ☐ Yes – Quote #: ________________________ ☐ No

✍️  SECTION 12 — AUTHORIZATION & SIGNATURES

By signing below, the customer acknowledges receipt of inspection findings and confirms the technician was granted access to all equipment. Technician certifies that all recorded data is accurate to the best of their knowledge.

| TECHNICIAN SIGNATURE Signature / Date | CUSTOMER / OWNER SIGNATURE Signature / Date |
| --- | --- |

| Print Name (Technician): ________________________ | Print Name (Customer): ________________________ |
| --- | --- |
| Certifications: EPA 608 ☐ NATE ☐ Other: ______ | Date Signed: ________________________ |
| Next Recommended Service: ________________________ | Next Scheduled Date: ________________________ |

🗂️  SECTION 13 — OFFICE USE ONLY

| Entered By: ________________________ | Date Entered: ________________________ |
| --- | --- |
| Work Order Closed: ☐ Yes ☐ No | Invoice Generated: ☐ Yes ☐ No Invoice #: ______ |
| Follow-Up Work Order Created: ☐ Yes WO #: ________ ☐ No | Warranty Call: ☐ Yes ☐ No |
| Checklist Scanned / Filed: ☐ Yes ☐ No | Customer Portal Updated: ☐ Yes ☐ No ☐ N/A |