| INSPECTION DETAILS Building / Facility Name: _________________________________ Property Address: _________________________________ City, State, ZIP: _________________________________ Owner / Property Manager: _________________________________ | TECHNICIAN & SERVICE INFO Technician Name: _________________________________ Tech ID / License #: _________________________________ Inspection Date: _________________________________ Inspection Type: _________________________________ |
| --- | --- |
| Unit / System ID: _________________________________ Equipment Tag #: _________________________________ Manufacturer: _________________________________ Model #: _________________________________ Serial #: _________________________________ | Inspection Type: _________________________________ Service Contract #: _________________________________ Last Service Date: _________________________________ Weather / Conditions: _________________________________ Ambient Temp (°F): _________________________________ |

| OVERALL STATUS | UNITS INSPECTED | ITEMS FAILED | FOLLOW-UP REQUIRED |
| --- | --- | --- | --- |
| ☐ Pass ☐ Fail ☐ Conditional |  |  | ☐ Yes ☐ No |

1. GENERAL UNIT & SYSTEM CONDITION

| Inspection Item | Pass | Fail | N/A | Reading / Measurement | Notes / Action Required |
| --- | --- | --- | --- | --- | --- |
| Unit/system is fully operational and running | ☐ | ☐ | ☐ |  |  |
| Nameplate data legible and matches records (model, serial, voltage, refrigerant) | ☐ | ☐ | ☐ |  |  |
| Equipment mounting and vibration isolators intact | ☐ | ☐ | ☐ |  |  |
| Sheet metal panels, access doors, and latches secure | ☐ | ☐ | ☐ |  |  |
| Unit base/curb free of rust, corrosion, and structural damage | ☐ | ☐ | ☐ |  |  |
| All access panels present, undamaged, and sealed | ☐ | ☐ | ☐ |  |  |
| Warning labels and safety decals in place and legible | ☐ | ☐ | ☐ |  |  |
| Electrical disconnect within sight of unit and functional | ☐ | ☐ | ☐ |  |  |
| Emergency shut-off accessible and labeled | ☐ | ☐ | ☐ |  |  |
| Area around unit clear of debris and obstructions (min. 36" clearance) | ☐ | ☐ | ☐ |  |  |

2. ELECTRICAL SYSTEM & CONTROLS

Electrical Components

| Inspection Item | Pass | Fail | N/A | Reading / Measurement | Notes / Action Required |
| --- | --- | --- | --- | --- | --- |
| Control panel / electrical box interior clean and dry | ☐ | ☐ | ☐ |  |  |
| All wiring connections tight, no loose terminals | ☐ | ☐ | ☐ |  |  |
| Wiring insulation intact — no fraying, chafing, or burn marks | ☐ | ☐ | ☐ |  |  |
| Contactors and relays in good condition (no pitting or burning) | ☐ | ☐ | ☐ |  |  |
| Capacitors within rated tolerance (start & run) | ☐ | ☐ | ☐ |  |  |
| Fuses and breakers correct size per equipment rating | ☐ | ☐ | ☐ |  |  |
| Disconnect fuses rated correctly for equipment | ☐ | ☐ | ☐ |  |  |
| Ground wires present and properly connected | ☐ | ☐ | ☐ |  |  |
| Low-voltage wiring routed and secured properly | ☐ | ☐ | ☐ |  |  |
| Control transformer output voltage within spec | ☐ | ☐ | ☐ |  |  |

Electrical Measurements

| Parameter | Measured | Unit | Spec / Range | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| Supply Voltage (L1-L2) |  | VAC | ±10% of nameplate |  |  |
| Supply Voltage (L1-L3) |  | VAC | ±10% of nameplate |  |  |
| Supply Voltage (L2-L3) |  | VAC | ±10% of nameplate |  |  |
| Voltage Imbalance |  | % | < 2% |  |  |
| Compressor RLA (Full Load) |  | A | Per nameplate |  |  |
| Compressor Amp Draw |  | A | ≤ 110% RLA |  |  |
| Condenser Fan Amp Draw |  | A | Per nameplate |  |  |
| Evaporator Fan Amp Draw |  | A | Per nameplate |  |  |
| Run Capacitor (Comp) |  | µF | ±6% of rated |  |  |
| Start Capacitor (if appl.) |  | µF | ±20% of rated |  |  |
| Control Transformer Output |  | VAC | 24–28 VAC |  |  |

Controls & Thermostat / BAS

| Inspection Item | Pass | Fail | N/A | Reading / Measurement | Notes / Action Required |
| --- | --- | --- | --- | --- | --- |
| Thermostat / controller setpoints correct for season | ☐ | ☐ | ☐ |  |  |
| Thermostat heating and cooling modes functional | ☐ | ☐ | ☐ |  |  |
| BAS/DDC points communicating correctly | ☐ | ☐ | ☐ |  |  |
| Economizer controls operational (if applicable) | ☐ | ☐ | ☐ |  |  |
| Demand control ventilation (DCV) operational (if applicable) | ☐ | ☐ | ☐ |  |  |
| Occupied/unoccupied scheduling programmed correctly | ☐ | ☐ | ☐ |  |  |
| Fault codes / alarm history reviewed and cleared | ☐ | ☐ | ☐ |  |  |
| Low-ambient controls operational (if applicable) | ☐ | ☐ | ☐ |  |  |

3. REFRIGERATION SYSTEM

Compressor

| Inspection Item | Pass | Fail | N/A | Reading / Measurement | Notes / Action Required |
| --- | --- | --- | --- | --- | --- |
| Compressor starts and runs without unusual noise or vibration | ☐ | ☐ | ☐ |  |  |
| Compressor crankcase heater operational (scroll/recip) | ☐ | ☐ | ☐ |  |  |
| Compressor oil level acceptable (sight glass if present) | ☐ | ☐ | ☐ |  |  |
| Compressor terminals and wiring tight and undamaged | ☐ | ☐ | ☐ |  |  |
| Compressor short-cycling not observed | ☐ | ☐ | ☐ |  |  |
| Compressor thermal overloads/protectors intact | ☐ | ☐ | ☐ |  |  |

Refrigerant Pressures & Temperatures

| Parameter | Measured | Unit | Spec / Range | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| Refrigerant Type |  |  | Per nameplate |  |  |
| Suction Pressure |  | PSIG | Per manufacturer |  |  |
| Discharge Pressure |  | PSIG | Per manufacturer |  |  |
| Suction Saturation Temp |  | °F | Per manufacturer |  |  |
| Discharge Saturation Temp |  | °F | Per manufacturer |  |  |
| Suction Line Temp |  | °F | Per manufacturer |  |  |
| Superheat (TXV system) |  | °F | 8–12°F typical |  |  |
| Subcooling (TXV system) |  | °F | 10–15°F typical |  |  |
| Superheat (Fixed Orifice) |  | °F | Per manufacturer chart |  |  |
| Approach Temp (condenser) |  | °F | Per manufacturer |  |  |

Refrigerant Circuit & Metering

| Inspection Item | Pass | Fail | N/A | Reading / Measurement | Notes / Action Required |
| --- | --- | --- | --- | --- | --- |
| Refrigerant charge within acceptable range (no undercharge/overcharge signs) | ☐ | ☐ | ☐ |  |  |
| No visible oil staining or refrigerant leak evidence at connections | ☐ | ☐ | ☐ |  |  |
| Electronic leak detection performed — no leaks detected | ☐ | ☐ | ☐ |  |  |
| TXV/EEV operation stable (no hunting) | ☐ | ☐ | ☐ |  |  |
| Liquid line sight glass — clear (no bubbles at full load) | ☐ | ☐ | ☐ |  |  |
| Filter drier condition acceptable (pressure drop < 2 PSID) | ☐ | ☐ | ☐ |  |  |
| Reversing valve operation correct — heating and cooling (heat pump) | ☐ | ☐ | ☐ |  |  |
| Check valve operation verified (if applicable) | ☐ | ☐ | ☐ |  |  |
| Refrigerant added this visit: _____ lbs of ___________ | ☐ | ☐ | ☐ |  |  |
| Refrigerant recovered this visit: _____ lbs | ☐ | ☐ | ☐ |  |  |

4. CONDENSER SECTION

| Inspection Item | Pass | Fail | N/A | Reading / Measurement | Notes / Action Required |
| --- | --- | --- | --- | --- | --- |
| Condenser coil clean and free of debris, dirt, and fin damage | ☐ | ☐ | ☐ |  |  |
| Condenser coil fins straight (< 10% fin damage acceptable) | ☐ | ☐ | ☐ |  |  |
| Condenser coil washed/cleaned this visit | ☐ | ☐ | ☐ |  |  |
| Condenser fan blades free of damage and balanced | ☐ | ☐ | ☐ |  |  |
| Condenser fan motor bearings — no noise or overheating | ☐ | ☐ | ☐ |  |  |
| Condenser fan motor shaft seal intact | ☐ | ☐ | ☐ |  |  |
| Condenser fan guard/screen present and secure | ☐ | ☐ | ☐ |  |  |
| Condenser fan rotation correct (pulling air through coil) | ☐ | ☐ | ☐ |  |  |
| Fan blade tip clearance within spec | ☐ | ☐ | ☐ |  |  |
| Head pressure control operational (staging/VFD if applicable) | ☐ | ☐ | ☐ |  |  |

Condenser Measurements

| Parameter | Measured | Unit | Spec / Range | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| Entering Air Temp (condenser) |  | °F | Ambient |  |  |
| Leaving Air Temp (condenser) |  | °F | 20–30°F above ambient |  |  |
| Condenser Fan Motor Amps |  | A | Per nameplate |  |  |
| Condenser Fan Voltage |  | VAC | Per nameplate |  |  |

5. EVAPORATOR / AIR HANDLER SECTION

Evaporator Coil & Drain

| Inspection Item | Pass | Fail | N/A | Reading / Measurement | Notes / Action Required |
| --- | --- | --- | --- | --- | --- |
| Evaporator coil clean and free of ice, dirt, and biological growth | ☐ | ☐ | ☐ |  |  |
| Evaporator coil fins straight (< 10% fin damage acceptable) | ☐ | ☐ | ☐ |  |  |
| Evaporator coil cleaned/treated this visit | ☐ | ☐ | ☐ |  |  |
| Condensate drain pan clean, no standing water or algae | ☐ | ☐ | ☐ |  |  |
| Condensate drain line clear and flowing freely | ☐ | ☐ | ☐ |  |  |
| Condensate drain trap properly sized and primed | ☐ | ☐ | ☐ |  |  |
| Secondary drain / overflow pan and alarm float operational | ☐ | ☐ | ☐ |  |  |
| Drain pan coating / liner intact (if applicable) | ☐ | ☐ | ☐ |  |  |
| No evidence of condensate overflow or water damage | ☐ | ☐ | ☐ |  |  |

Supply / Evaporator Fan & Motor

| Inspection Item | Pass | Fail | N/A | Reading / Measurement | Notes / Action Required |
| --- | --- | --- | --- | --- | --- |
| Blower/fan wheel clean and free of buildup | ☐ | ☐ | ☐ |  |  |
| Blower wheel balanced — no vibration or noise | ☐ | ☐ | ☐ |  |  |
| Blower wheel set screws tight on shaft | ☐ | ☐ | ☐ |  |  |
| Belt drive: belt tension and condition acceptable (if applicable) | ☐ | ☐ | ☐ |  |  |
| Belt drive: pulleys aligned (if applicable) | ☐ | ☐ | ☐ |  |  |
| Blower motor bearings lubricated or sealed — no noise | ☐ | ☐ | ☐ |  |  |
| Blower motor operating temperature acceptable (< 40°C rise) | ☐ | ☐ | ☐ |  |  |
| Fan VFD operational and parameters set correctly (if applicable) | ☐ | ☐ | ☐ |  |  |
| Airflow direction correct through coil | ☐ | ☐ | ☐ |  |  |

Air Handling Measurements

| Parameter | Measured | Unit | Spec / Range | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| Supply Air Temperature |  | °F | Per design / setpoint |  |  |
| Return Air Temperature |  | °F | Per design |  |  |
| Delta T (Return – Supply) |  | °F | 16–22°F typical cooling |  |  |
| Supply Air Static Pressure |  | in WC | Per design |  |  |
| Return Air Static Pressure |  | in WC | Per design |  |  |
| Total External Static Pressure |  | in WC | ≤ unit rated TESP |  |  |
| Airflow (CFM) |  | CFM | Per design |  |  |
| Supply Fan Motor Amps |  | A | Per nameplate |  |  |
| Evaporator Coil Pressure Drop |  | in WC | Per manufacturer |  |  |
| Relative Humidity (return) |  | %RH | 40–60% typical |  |  |

6. FILTERS, INDOOR AIR QUALITY & VENTILATION

| Inspection Item | Pass | Fail | N/A | Reading / Measurement | Notes / Action Required |
| --- | --- | --- | --- | --- | --- |
| Return air filters inspected — not excessively dirty or damaged | ☐ | ☐ | ☐ |  |  |
| Filters replaced this visit (note size/MERV: ____________) | ☐ | ☐ | ☐ |  |  |
| Filter rack / frame seals intact — no bypass | ☐ | ☐ | ☐ |  |  |
| Filter media type matches specification (MERV rating: ____) | ☐ | ☐ | ☐ |  |  |
| Pre-filters inspected and replaced (if two-stage filtration) | ☐ | ☐ | ☐ |  |  |
| HEPA / final filters inspected (if applicable) | ☐ | ☐ | ☐ |  |  |
| Fresh air / outside air damper operational and opening correctly | ☐ | ☐ | ☐ |  |  |
| Minimum outside air CFM verified (DCV or fixed %) | ☐ | ☐ | ☐ |  |  |
| Economizer damper fully operational (if applicable) | ☐ | ☐ | ☐ |  |  |
| Economizer low-limit controls functional (temp & enthalpy) | ☐ | ☐ | ☐ |  |  |
| Relief / exhaust dampers open and close properly | ☐ | ☐ | ☐ |  |  |
| UV germicidal lights operational and bulbs within service life (if appl.) | ☐ | ☐ | ☐ |  |  |
| Bipolar ionization system operational (if applicable) | ☐ | ☐ | ☐ |  |  |
| Energy recovery wheel / core clean and rotating (if applicable) | ☐ | ☐ | ☐ |  |  |

Indoor Air Quality Measurements

| Parameter | Measured | Unit | Spec / Range | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| CO2 Level (occupied space) |  | ppm | < 1100 ppm (ASHRAE 62.1) |  |  |
| CO Level (mechanical room) |  | ppm | < 35 ppm (OSHA PEL) |  |  |
| Space Relative Humidity |  | %RH | 30–60% |  |  |
| Space Temperature |  | °F | Per setpoint |  |  |
| Filter Pressure Drop |  | in WC | Per filter manufacturer |  |  |
| OA Damper Position |  | % | Per design minimum |  |  |

7. DUCTWORK, DISTRIBUTION & TERMINAL UNITS

| Inspection Item | Pass | Fail | N/A | Reading / Measurement | Notes / Action Required |
| --- | --- | --- | --- | --- | --- |
| Supply ductwork free of visible damage, holes, or disconnections | ☐ | ☐ | ☐ |  |  |
| Return ductwork sealed — no unintentional air pathways | ☐ | ☐ | ☐ |  |  |
| Flexible duct connections secure and not kinked or compressed | ☐ | ☐ | ☐ |  |  |
| Duct insulation intact — no tears, gaps, or moisture damage | ☐ | ☐ | ☐ |  |  |
| Supply air grilles/diffusers clean and unobstructed | ☐ | ☐ | ☐ |  |  |
| Return air grilles clean and unobstructed | ☐ | ☐ | ☐ |  |  |
| VAV boxes / fan-powered terminals operational | ☐ | ☐ | ☐ |  |  |
| VAV box actuators functional — stroke verified | ☐ | ☐ | ☐ |  |  |
| VAV box minimum/maximum CFM setpoints correct | ☐ | ☐ | ☐ |  |  |
| Zone dampers (if applicable) moving freely | ☐ | ☐ | ☐ |  |  |
| Smoke/fire dampers accessible and operational | ☐ | ☐ | ☐ |  |  |
| Fire damper inspection/test within required interval | ☐ | ☐ | ☐ |  |  |
| Duct leakage within acceptable limits | ☐ | ☐ | ☐ |  |  |

8. HEATING SYSTEM (GAS, ELECTRIC, HYDRONIC)

Gas-Fired Components (if applicable)

| Inspection Item | Pass | Fail | N/A | Reading / Measurement | Notes / Action Required |
| --- | --- | --- | --- | --- | --- |
| Gas valve operation — opens and closes cleanly | ☐ | ☐ | ☐ |  |  |
| Ignition system functional (ignitor/spark) | ☐ | ☐ | ☐ |  |  |
| Burner flames — steady, blue, properly shaped | ☐ | ☐ | ☐ |  |  |
| Heat exchanger visually inspected — no cracks or holes | ☐ | ☐ | ☐ |  |  |
| Flue / vent pipes secured, sloped, and undamaged | ☐ | ☐ | ☐ |  |  |
| Combustion air supply adequate and unobstructed | ☐ | ☐ | ☐ |  |  |
| Draft inducer / induced draft fan operational | ☐ | ☐ | ☐ |  |  |
| Pressure switches and safety controls functional | ☐ | ☐ | ☐ |  |  |
| High-limit safety switch operational | ☐ | ☐ | ☐ |  |  |
| Gas supply pressure within spec | ☐ | ☐ | ☐ |  |  |
| Manifold gas pressure within spec | ☐ | ☐ | ☐ |  |  |
| CO sampling at supply register and flue | ☐ | ☐ | ☐ |  |  |

Heating Measurements

| Parameter | Measured | Unit | Spec / Range | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| Supply Gas Pressure |  | in WC | 7.0 (nat. gas typical) |  |  |
| Manifold Gas Pressure |  | in WC | 3.5 (nat. gas typical) |  |  |
| Flue Gas Temperature |  | °F | Per manufacturer |  |  |
| CO at Supply Register |  | ppm | < 9 ppm per ASHRAE 62 |  |  |
| CO at Flue (undiluted) |  | ppm | < 400 ppm (AGA test) |  |  |
| Heating Delta T |  | °F | Per design |  |  |
| High-Limit Switch Trip Temp |  | °F | Per nameplate |  |  |

Electric Heat / Heat Pump (if applicable)

| Inspection Item | Pass | Fail | N/A | Reading / Measurement | Notes / Action Required |
| --- | --- | --- | --- | --- | --- |
| Electric heat strips free of buildup and damage | ☐ | ☐ | ☐ |  |  |
| Electric heat staging correct per outdoor temp | ☐ | ☐ | ☐ |  |  |
| Defrost cycle operational — heat pump (if applicable) | ☐ | ☐ | ☐ |  |  |
| Defrost controls — termination by time/temp/pressure correct | ☐ | ☐ | ☐ |  |  |
| Auxiliary heat lockout set correctly | ☐ | ☐ | ☐ |  |  |
| Supplemental / emergency heat functional | ☐ | ☐ | ☐ |  |  |

9. HYDRONIC SYSTEMS (CHILLER, BOILER & PIPING)

Piping & System Condition

| Inspection Item | Pass | Fail | N/A | Reading / Measurement | Notes / Action Required |
| --- | --- | --- | --- | --- | --- |
| No visible leaks at pipe joints, valves, or fittings | ☐ | ☐ | ☐ |  |  |
| Piping insulation intact — no gaps, moisture, or damage | ☐ | ☐ | ☐ |  |  |
| Flexible connectors in good condition (no cracking) | ☐ | ☐ | ☐ |  |  |
| Balancing valves in correct position | ☐ | ☐ | ☐ |  |  |
| Isolation valves operational and not seized | ☐ | ☐ | ☐ |  |  |
| Strainers inspected and cleaned | ☐ | ☐ | ☐ |  |  |
| Air separator and automatic air vents functional | ☐ | ☐ | ☐ |  |  |
| Expansion tank pre-charge pressure correct | ☐ | ☐ | ☐ |  |  |
| System fill valve and backflow preventer operational | ☐ | ☐ | ☐ |  |  |
| Chemical treatment program current — water test performed | ☐ | ☐ | ☐ |  |  |

Hydronic Measurements

| Parameter | Measured | Unit | Spec / Range | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| System Operating Pressure |  | PSIG | Per design |  |  |
| Expansion Tank Pressure |  | PSIG | Per design |  |  |
| Chilled Water Supply Temp |  | °F | 44–48°F typical |  |  |
| Chilled Water Return Temp |  | °F | 54–58°F typical |  |  |
| CHW Delta T |  | °F | 10–14°F typical |  |  |
| Hot Water Supply Temp |  | °F | 140–180°F typical |  |  |
| Hot Water Return Temp |  | °F | Per design |  |  |
| HW Delta T |  | °F | Per design |  |  |
| Pump Differential Pressure |  | PSID | Per design |  |  |
| Water pH Level |  | pH | 7.0–9.0 |  |  |
| Inhibitor Level |  | ppm | Per chemical supplier |  |  |
| Glycol Concentration |  | % | Per design freeze protection |  |  |

Pumps & Pump Motors

| Inspection Item | Pass | Fail | N/A | Reading / Measurement | Notes / Action Required |
| --- | --- | --- | --- | --- | --- |
| Pump operating without noise or vibration | ☐ | ☐ | ☐ |  |  |
| Pump mechanical seal — no leaking | ☐ | ☐ | ☐ |  |  |
| Pump motor bearings lubricated (if serviceable) | ☐ | ☐ | ☐ |  |  |
| Pump motor amp draw within nameplate rating | ☐ | ☐ | ☐ |  |  |
| Pump VFD operational and parameters correct (if applicable) | ☐ | ☐ | ☐ |  |  |
| Standby pump operational — lead/lag switchover tested | ☐ | ☐ | ☐ |  |  |

10. SAFETY DEVICES, CODE COMPLIANCE & DOCUMENTATION

| Inspection Item | Pass | Fail | N/A | Reading / Measurement | Notes / Action Required |
| --- | --- | --- | --- | --- | --- |
| High-pressure safety cutout set and tested | ☐ | ☐ | ☐ |  |  |
| Low-pressure safety cutout set and tested | ☐ | ☐ | ☐ |  |  |
| Freeze protection thermostat / aquastat set and tested | ☐ | ☐ | ☐ |  |  |
| Low ambient temperature controls operational | ☐ | ☐ | ☐ |  |  |
| Condensate overflow / secondary pan switch tested | ☐ | ☐ | ☐ |  |  |
| Belt / shaft guards in place and secure | ☐ | ☐ | ☐ |  |  |
| Lock-Out / Tag-Out (LOTO) procedures followed during service | ☐ | ☐ | ☐ |  |  |
| Refrigerant cylinder(s) properly stored and labeled on site | ☐ | ☐ | ☐ |  |  |
| Safety Data Sheets (SDS) for refrigerant on file | ☐ | ☐ | ☐ |  |  |
| EPA Section 608 certification on file for technician | ☐ | ☐ | ☐ |  |  |
| Equipment within permit / inspection compliance | ☐ | ☐ | ☐ |  |  |
| Unit operating hours / runtime log updated | ☐ | ☐ | ☐ |  |  |
| Previous inspection deficiencies corrected | ☐ | ☐ | ☐ |  |  |

11. DEFICIENCY LOG & CORRECTIVE ACTION PLAN

| # | Sect. | Deficiency Description | Priority | Est. Cost | Target Date | Resolution / Parts Needed |
| --- | --- | --- | --- | --- | --- | --- |
| 1 |  |  | ☐ Critical ☐ High ☐ Medium ☐ Low | $ |  |  |
| 2 |  |  | ☐ Critical ☐ High ☐ Medium ☐ Low | $ |  |  |
| 3 |  |  | ☐ Critical ☐ High ☐ Medium ☐ Low | $ |  |  |
| 4 |  |  | ☐ Critical ☐ High ☐ Medium ☐ Low | $ |  |  |
| 5 |  |  | ☐ Critical ☐ High ☐ Medium ☐ Low | $ |  |  |
| 6 |  |  | ☐ Critical ☐ High ☐ Medium ☐ Low | $ |  |  |
| 7 |  |  | ☐ Critical ☐ High ☐ Medium ☐ Low | $ |  |  |
| 8 |  |  | ☐ Critical ☐ High ☐ Medium ☐ Low | $ |  |  |

Priority Guide: Critical = Safety hazard / unit offline  |  High = Failure imminent (< 30 days)  |  Medium = Degraded efficiency (30–90 days)  |  Low = Preventive / cosmetic (> 90 days)

12. MAINTENANCE PERFORMED THIS VISIT

| Tasks Completed (check all that apply): ☐ Air filters replaced ☐ Coils cleaned (evap) ☐ Coils cleaned (cond) ☐ Condensate drain flushed ☐ Refrigerant leak check ☐ Electrical connections tightened ☐ Capacitors tested / replaced ☐ Belts inspected / replaced ☐ Bearings lubricated ☐ Economizer serviced ☐ Controls calibrated ☐ Refrigerant added (lbs: ____) ☐ Water treatment tested ☐ Strainers cleaned ☐ Other: ___________________________ | Materials & Parts Used: Item / Part #; Qty; Unit Cost. $. $. $. $. $. $. $. $. |
| --- | --- |

13. PHOTOS, ATTACHMENTS & DOCUMENTATION

| # | Photo / Document Description | File Name / Ref # | Notes |
| --- | --- | --- | --- |
| 1 |  |  |  |
| 2 |  |  |  |
| 3 |  |  |  |
| 4 |  |  |  |
| 5 |  |  |  |
| 6 |  |  |  |

Attachments included:

☐ Refrigerant Log   ☐ TAB Report   ☐ Combustion Analysis Report   ☐ Water Treatment Report   ☐ Electrical Test Results   ☐ Warranty Documents   ☐ Other: ___________

14. INSPECTION SUMMARY & SIGNATURES

Overall System Assessment / Inspector Notes: __________________________________________________________________________________________________________________________________ __________________________________________________________________________________________________________________________________ __________________________________________________________________________________________________________________________________ __________________________________________________________________________________________________________________________________ __________________________________________________________________________________________________________________________________

| INSPECTOR / TECHNICIAN Name: ___________________________________ Title / License #: ___________________________________ Company: ___________________________________ Signature: ___________________________________ Date: ___________________________________ | CLIENT / FACILITY REPRESENTATIVE Name: ___________________________________ Title: ___________________________________ Company: ___________________________________ Signature: ___________________________________ Date: ___________________________________ |
| --- | --- |

This inspection checklist is a professional assessment tool. Findings and recommendations do not constitute a guarantee of system performance. Retain completed forms for a minimum of 3 years.