HVAC HOME INSPECTION CHECKLIST Residential HVAC system evaluation for home buyers, sellers, and homeowners. Rate each item: ✅ Acceptable ⚠️ Monitor ⛔ Deficient — Repair Needed.

| ✅ ACCEPTABLE Item is in satisfactory working condition | ⚠️ MONITOR Functional but aging or marginal — plan for replacement | ⛔ DEFICIENT Repair or replace recommended before / at closing | N/A NOT APPLICABLE Item not present or not applicable to this home |
| --- | --- | --- | --- |

🏠  SECTION 1 — INSPECTION & PROPERTY INFORMATION

| Inspection Report #: ________________________ | Inspection Date: ________________________ |
| --- | --- |
| Inspector Name: ________________________ | Inspector License #: ________________________ |
| Inspection Company: ________________________ | Phone: ________________________ |
| Property Address: ________________________ | City / State / ZIP: ________________________ |
| Client / Buyer Name: ________________________ | Client Phone / Email: ________________________ |
| Home Owner (if different): ________________________ | Real Estate Agent: ________________________ |
| Home Type: ☐ Single Family ☐ Townhome ☐ Condo ☐ Multi-Family | Year Built: ____________ |
| Sq. Footage: ____________ sq ft | Floors: ______ Basement: ☐ Yes ☐ No |
| Inspection Purpose: ☐ Buyer ☐ Pre-Listing ☐ Annual ☐ Insurance ☐ Other: | Outdoor Temp at Inspection: ______°F Humidity: _____% |
| Systems Powered On: ☐ Yes – all ☐ Partial (note below) ☐ No – could not test | Thermostat Accessible: ☐ Yes ☐ No ☐ Smart/App Only |

⚙️  SECTION 2 — HVAC SYSTEM IDENTIFICATION

Primary Heating System

| Heating System Type: ☐ Gas Furnace ☐ Heat Pump ☐ Electric ☐ Boiler ☐ Other: | Fuel Source: ☐ Natural Gas ☐ Propane ☐ Electric ☐ Oil |
| --- | --- |
| Brand / Manufacturer: ________________________ | Model #: ________________________ |
| Serial #: ________________________ | Manufacture / Install Year: ________________________ |
| Estimated Age: ____________ years | Expected Lifespan: 15–20 yrs typical |
| Location: ☐ Basement ☐ Closet ☐ Attic ☐ Crawl Space ☐ Garage | Heating Capacity (BTU/hr): ________________________ |

Primary Cooling System

| Cooling System Type: ☐ Central A/C ☐ Heat Pump ☐ Mini-Split ☐ Window Units ☐ None | Refrigerant Type: ☐ R-22 ☐ R-410A ☐ R-454B ☐ Unknown |
| --- | --- |
| Brand / Manufacturer: ________________________ | Model #: ________________________ |
| Serial #: ________________________ | Manufacture / Install Year: ________________________ |
| Estimated Age: ____________ years | Expected Lifespan: 12–18 yrs typical |
| Cooling Capacity (Tons): _______ tons | Outdoor Unit Location: ________________________ |

Additional Systems

| Number of Zones: ______ | Zone Control Brand: ________________________ |
| --- | --- |
| Water Heater (if HVAC-linked): ☐ Tankless ☐ Tank ☐ Heat Pump WH ☐ None | Water Heater Age: ____________ years |
| Whole-Home Humidifier: ☐ Yes — Brand: ____________ ☐ No | Whole-Home Dehumidifier: ☐ Yes — Brand: ____________ ☐ No |
| ERV / HRV: ☐ Yes — Brand: ____________ ☐ No | Air Purifier / UV: ☐ Yes — Brand: ____________ ☐ No |

🌡️  SECTION 3 — THERMOSTAT & CONTROLS

| Thermostat Brand / Model: ________________________ | Type: ☐ Manual ☐ Programmable ☐ Smart/WiFi |
| --- | --- |
| Thermostat Location: ________________________ | Thermostat Age: ____________ years |
| Set to Cool — Tested: ☐ Yes ☐ No ☐ N/A (season) | Set to Heat — Tested: ☐ Yes ☐ No ☐ N/A (season) |
| Temperature Displayed: ______°F | Matches Actual Temp (±2°F): ☐ Yes ☐ No |

| Thermostat & Control Item | ✅ OK | ⚠️ Monitor | ⛔ Deficient | Notes / Age / Est. Cost |
| --- | --- | --- | --- | --- |
| Thermostat – level, secure, reads correct temperature | ☐ | ☐ | ☐ |  |
| Display functioning – no error codes or blank screen | ☐ | ☐ | ☐ |  |
| Cool mode – compressor and fan respond within 3 minutes | ☐ | ☐ | ☐ |  |
| Heat mode – heating system responds correctly | ☐ | ☐ | ☐ |  |
| Fan-only mode – air handler runs independently | ☐ | ☐ | ☐ |  |
| Batteries replaced / wired power confirmed | ☐ | ☐ | ☐ |  |
| Zoning panel – all zones respond, no fault lights | ☐ | ☐ | ☐ |  |
| Smart thermostat – connected, app accessible (if applicable) | ☐ | ☐ | ☐ |  |

🔥  SECTION 4 — FURNACE / AIR HANDLER INSPECTION

| Return Air Temp: ______°F | Supply Air Temp: ______°F |
| --- | --- |
| Temperature Rise (ΔT): ______°F (target: 16–22°F cooling / per spec heat) | Static Pressure – Total: ______ in. w.c. |
| Gas Pressure (manifold): ______ in. w.c. (typical: 3.5" nat gas) | CO at Return Grille: ______ ppm (safe: <9 ppm) |

| Furnace / Air Handler Item | ✅ OK | ⚠️ Monitor | ⛔ Deficient | Notes / Age / Est. Cost |
| --- | --- | --- | --- | --- |
| Cabinet & Access |  |  |  |  |
| Unit cabinet – no rust, dents, or open holes in housing | ☐ | ☐ | ☐ |  |
| Access panels – present, secured, safety switch functional | ☐ | ☐ | ☐ |  |
| Clearances maintained – no storage within required clearance | ☐ | ☐ | ☐ |  |
| Unit level and properly supported | ☐ | ☐ | ☐ |  |
| Filter |  |  |  |  |
| Air filter present and correctly sized | ☐ | ☐ | ☐ |  |
| Filter condition – clean / acceptable (replace if dirty) | ☐ | ☐ | ☐ |  |
| Filter slot sealed – no air bypass around filter frame | ☐ | ☐ | ☐ |  |
| Blower & Motor |  |  |  |  |
| Blower wheel – clean, no debris, no wobble or vibration | ☐ | ☐ | ☐ |  |
| Blower motor – runs quietly, no burning smell | ☐ | ☐ | ☐ |  |
| Belt (if belt-drive) – correct tension, no cracks or glazing | ☐ | ☐ | ☐ |  |
| Heat Exchanger (Gas Furnace) |  |  |  |  |
| Heat exchanger – no visible cracks or holes (CO test negative) | ☐ | ☐ | ☐ |  |
| No evidence of soot or CO staining on furnace exterior | ☐ | ☐ | ☐ |  |
| Flame pattern – blue, steady, no yellow tips or rollout | ☐ | ☐ | ☐ |  |
| Burner ignition – starts within 3 attempts, no lockout | ☐ | ☐ | ☐ |  |
| Limit switch – not tripped, no sign of overheating | ☐ | ☐ | ☐ |  |
| Heat Strips (Electric / Heat Pump Backup) |  |  |  |  |
| All elements operational – amp draw within spec | ☐ | ☐ | ☐ |  |
| Sequencers – staged correctly, no simultaneous full-load draw | ☐ | ☐ | ☐ |  |
| Gas Supply |  |  |  |  |
| Gas shutoff valve – accessible, correct position | ☐ | ☐ | ☐ |  |
| Gas piping – no corrosion, proper support, no odor | ☐ | ☐ | ☐ |  |
| Flex gas connector – not kinked, within service life | ☐ | ☐ | ☐ |  |
| Venting & Combustion Air |  |  |  |  |
| Flue / vent pipe – properly sized, sloped, no blockage | ☐ | ☐ | ☐ |  |
| Vent pipe joints – secured, no gaps or backdraft | ☐ | ☐ | ☐ |  |
| Combustion air opening – unobstructed, correct free area | ☐ | ☐ | ☐ |  |
| PVC vent (high-efficiency) – no cracks, proper pitch, drain trap clear | ☐ | ☐ | ☐ |  |
| Condensate |  |  |  |  |
| Condensate drain pan – clean, no standing water, no rust | ☐ | ☐ | ☐ |  |
| Condensate drain line – clear, no blockage, properly pitched | ☐ | ☐ | ☐ |  |
| Condensate trap – primed, no visible cracks | ☐ | ☐ | ☐ |  |
| Condensate pump (if present) – operates, float switch functional | ☐ | ☐ | ☐ |  |

❄️  SECTION 5 — AIR CONDITIONER / HEAT PUMP (OUTDOOR UNIT)

| Suction Line Temp: ______°F | Liquid Line Temp: ______°F |
| --- | --- |
| Estimated ΔT (supply vs return): ______°F (target: 16–22°F) | Unit Running at Time of Inspection: ☐ Yes ☐ No ☐ Temp too cold to test |

| A/C & Outdoor Unit Item | ✅ OK | ⚠️ Monitor | ⛔ Deficient | Notes / Age / Est. Cost |
| --- | --- | --- | --- | --- |
| Structure & Placement |  |  |  |  |
| Unit pad / mount – level, stable, not sunken or cracked | ☐ | ☐ | ☐ |  |
| Service clearances – 12" min. sides, 24" front service access | ☐ | ☐ | ☐ |  |
| No vegetation or debris within 18" of unit | ☐ | ☐ | ☐ |  |
| Unit housing – no significant rust, damage, or missing panels | ☐ | ☐ | ☐ |  |
| Coil & Fan |  |  |  |  |
| Condenser coil – clean, fins straight, no blockage | ☐ | ☐ | ☐ |  |
| Coil fins – not significantly bent or crushed (>20% restriction noted) | ☐ | ☐ | ☐ |  |
| Condenser fan blade – no cracks, tight on shaft, correct pitch | ☐ | ☐ | ☐ |  |
| Condenser fan motor – correct rotation, no abnormal noise | ☐ | ☐ | ☐ |  |
| Compressor |  |  |  |  |
| Compressor – starts and runs, no abnormal noise or vibration | ☐ | ☐ | ☐ |  |
| No oil staining on compressor body or around service valves | ☐ | ☐ | ☐ |  |
| Compressor sounds – no loud clicking, grinding, or squealing | ☐ | ☐ | ☐ |  |
| Electrical |  |  |  |  |
| Disconnect – present within sight of unit, correct amp rating | ☐ | ☐ | ☐ |  |
| Wiring – conduit intact, no exposed conductors | ☐ | ☐ | ☐ |  |
| Contactor – no visible pitting, energizes on call | ☐ | ☐ | ☐ |  |
| Capacitor – no bulging or leaking (visual check) | ☐ | ☐ | ☐ |  |
| Refrigerant Lines |  |  |  |  |
| Suction line insulation – intact, not torn or missing | ☐ | ☐ | ☐ |  |
| Line set – properly supported, no kinks or sharp bends | ☐ | ☐ | ☐ |  |
| No visible oil staining indicating refrigerant leak | ☐ | ☐ | ☐ |  |
| Service valve caps – present on both valves | ☐ | ☐ | ☐ |  |
| Heat Pump — Additional |  |  |  |  |
| Reversing valve – cycles correctly between heat and cool modes | ☐ | ☐ | ☐ |  |
| Defrost operation – tested or evidence of proper function | ☐ | ☐ | ☐ |  |
| Auxiliary / emergency heat – operational backup confirmed | ☐ | ☐ | ☐ |  |

🌀  SECTION 6 — EVAPORATOR COIL & INDOOR REFRIGERATION

| Evaporator Coil & Indoor Refrigeration Item | ✅ OK | ⚠️ Monitor | ⛔ Deficient | Notes / Age / Est. Cost |
| --- | --- | --- | --- | --- |
| Evaporator coil – accessible for inspection (access panel present) | ☐ | ☐ | ☐ |  |
| Coil surface – clean, no heavy dirt, microbial growth, or ice | ☐ | ☐ | ☐ |  |
| No ice formation on coil or suction line during operation | ☐ | ☐ | ☐ |  |
| No visible refrigerant leak – no oil staining at coil connections | ☐ | ☐ | ☐ |  |
| Coil housing – no air bypass around coil frame | ☐ | ☐ | ☐ |  |
| TXV / metering device – no visible damage or icing | ☐ | ☐ | ☐ |  |
| Suction line (indoor) – insulated, no sweating on insulation exterior | ☐ | ☐ | ☐ |  |
| Coil drain pan – clean, no standing water, properly pitched | ☐ | ☐ | ☐ |  |

📐  SECTION 7 — DUCTWORK, AIRFLOW & DISTRIBUTION

| Duct Material: ☐ Sheet Metal ☐ Flex ☐ Fiberglass Board ☐ Mixed | Duct Location: ☐ Attic ☐ Basement ☐ Crawl ☐ Conditioned |
| --- | --- |
| Supply Registers – Qty: ______ | Return Grilles – Qty: ______ |
| Duct Insulation R-Value (observed): R-______ | Noted Duct Leakage (visible): ☐ None ☐ Minor ☐ Significant |

| Ductwork & Airflow Item | ✅ OK | ⚠️ Monitor | ⛔ Deficient | Notes / Age / Est. Cost |
| --- | --- | --- | --- | --- |
| Supply System |  |  |  |  |
| Supply ducts – no visible disconnections, collapses, or major leaks | ☐ | ☐ | ☐ |  |
| Supply registers – present in all conditioned rooms, not blocked | ☐ | ☐ | ☐ |  |
| Supply airflow felt at each register (spot check) | ☐ | ☐ | ☐ |  |
| Supply plenum – insulated, sealed at AHU connection, no holes | ☐ | ☐ | ☐ |  |
| Return System |  |  |  |  |
| Return grilles – unobstructed, not blocked by furniture or drapes | ☐ | ☐ | ☐ |  |
| Return air area sufficient – not undersized relative to system | ☐ | ☐ | ☐ |  |
| Return ducts – no disconnects or unintentional air paths | ☐ | ☐ | ☐ |  |
| Duct Condition |  |  |  |  |
| Flex duct – not kinked, compressed, or excessively long | ☐ | ☐ | ☐ |  |
| Duct insulation – intact, no damage or missing sections | ☐ | ☐ | ☐ |  |
| Duct connections – taped or mastic-sealed (not just raw sheet metal) | ☐ | ☐ | ☐ |  |
| No evidence of pest infestation or moisture inside ducts | ☐ | ☐ | ☐ |  |
| Unconditioned space ducts – insulated to current code (R-8 attic, R-6 crawl) | ☐ | ☐ | ☐ |  |
| Zoning (if applicable) |  |  |  |  |
| Zone dampers – respond correctly to thermostat calls | ☐ | ☐ | ☐ |  |
| Bypass damper – present and operational (if required by zoning design) | ☐ | ☐ | ☐ |  |

🌬️  SECTION 8 — INDOOR AIR QUALITY & VENTILATION

| Indoor Relative Humidity: ______%RH (target: 40–60%) | CO Level (ambient): ______ ppm (safe: <9 ppm) |
| --- | --- |
| CO₂ Level: ______ ppm (target: <1100 ppm occupied) | Visible Mold Suspected: ☐ None ☐ Suspected — note location |

| IAQ & Ventilation Item | ✅ OK | ⚠️ Monitor | ⛔ Deficient | Notes / Age / Est. Cost |
| --- | --- | --- | --- | --- |
| Air Quality |  |  |  |  |
| No musty or moldy odors from supply registers | ☐ | ☐ | ☐ |  |
| No evidence of mold growth in/on AHU, coil, or ducts | ☐ | ☐ | ☐ |  |
| No burning, chemical, or exhaust odors during operation | ☐ | ☐ | ☐ |  |
| CO detector present within 15 ft of fuel-burning appliance | ☐ | ☐ | ☐ |  |
| Smoke detectors present and within replacement date | ☐ | ☐ | ☐ |  |
| Filtration & Purification |  |  |  |  |
| Standard filter – present, correctly sized, condition acceptable | ☐ | ☐ | ☐ |  |
| Media filter (4" or 5") – within replacement interval | ☐ | ☐ | ☐ |  |
| HEPA filter – present and serviceable (if equipped) | ☐ | ☐ | ☐ |  |
| Electronic air cleaner – cells clean, ionizer wires intact | ☐ | ☐ | ☐ |  |
| UV germicidal lamp – bulb within service life (12–24 months typical) | ☐ | ☐ | ☐ |  |
| Ventilation |  |  |  |  |
| Bathroom exhaust fans – vent to exterior (not into attic) | ☐ | ☐ | ☐ |  |
| Kitchen exhaust – ducted to exterior or recirculating (note type) | ☐ | ☐ | ☐ |  |
| ERV / HRV – core clean, balanced, dampers operational | ☐ | ☐ | ☐ |  |
| Fresh air intake – present and unobstructed (if required by code) | ☐ | ☐ | ☐ |  |
| Humidity Control |  |  |  |  |
| Whole-home humidifier – water panel / drum inspected | ☐ | ☐ | ☐ |  |
| Humidifier bypass damper – summer position correct | ☐ | ☐ | ☐ |  |
| Whole-home dehumidifier – drain clear, operational | ☐ | ☐ | ☐ |  |

🏗️  SECTION 9 — ATTIC, CRAWL SPACE & MECHANICAL ROOM

| Attic, Crawl & Mechanical Room Item | ✅ OK | ⚠️ Monitor | ⛔ Deficient | Notes / Age / Est. Cost |
| --- | --- | --- | --- | --- |
| Attic (if HVAC present) |  |  |  |  |
| Attic insulation – adequate depth (R-38 min. per modern code) | ☐ | ☐ | ☐ |  |
| Attic ventilation – adequate soffit / ridge vents, no blocked baffles | ☐ | ☐ | ☐ |  |
| No HVAC equipment visible through vapor barrier tears or insulation gaps | ☐ | ☐ | ☐ |  |
| Attic AHU / ducts – insulated, drip pan with float switch present | ☐ | ☐ | ☐ |  |
| No evidence of pest damage to duct insulation or wiring | ☐ | ☐ | ☐ |  |
| Crawl Space (if HVAC present) |  |  |  |  |
| Vapor barrier – present, >6 mil, minimal tears | ☐ | ☐ | ☐ |  |
| Crawl ventilation – adequate vents or conditioned crawl with sealed walls | ☐ | ☐ | ☐ |  |
| Ducts in crawl – insulated, not laying in water or on ground | ☐ | ☐ | ☐ |  |
| No standing water under or near any HVAC components | ☐ | ☐ | ☐ |  |
| No significant mold, rot, or pest damage observed | ☐ | ☐ | ☐ |  |
| Mechanical Room / Utility Closet |  |  |  |  |
| Adequate service clearance in front of furnace (30" min.) | ☐ | ☐ | ☐ |  |
| Combustion air source – adequate for equipment BTU input | ☐ | ☐ | ☐ |  |
| No storage of flammable materials within appliance clearances | ☐ | ☐ | ☐ |  |
| Door undercut / grille – adequate return air path | ☐ | ☐ | ☐ |  |
| Floor drain present and clear (water heater, A-coil drip) | ☐ | ☐ | ☐ |  |

🛡️  SECTION 10 — SAFETY DEVICES & CODE COMPLIANCE

| Safety Device / Code Compliance Item | ✅ OK | ⚠️ Monitor | ⛔ Deficient | Notes / Age / Est. Cost |
| --- | --- | --- | --- | --- |
| Combustion Safety |  |  |  |  |
| CO detector – present, tested, in date (replace every 5–7 years) | ☐ | ☐ | ☐ |  |
| Gas leak – no odor, electronic sniffer negative (if tested) | ☐ | ☐ | ☐ |  |
| Flame rollout shield / switch – intact, not bypassed | ☐ | ☐ | ☐ |  |
| High-limit switch – operational, not manually reset / bypassed | ☐ | ☐ | ☐ |  |
| Electrical Safety |  |  |  |  |
| Equipment disconnect – present, within sight of unit, labeled | ☐ | ☐ | ☐ |  |
| Overcurrent protection – correct amperage per nameplate | ☐ | ☐ | ☐ |  |
| Equipment grounded – grounding conductor visible | ☐ | ☐ | ☐ |  |
| GFCI protection – present in mechanical rooms per applicable code | ☐ | ☐ | ☐ |  |
| Condensate Safety |  |  |  |  |
| Primary and secondary condensate drains present (attic / closet AHU) | ☐ | ☐ | ☐ |  |
| Float / overflow switch – operational, shuts down unit on overflow | ☐ | ☐ | ☐ |  |
| No evidence of past condensate overflow or water staining on ceiling | ☐ | ☐ | ☐ |  |
| General Code |  |  |  |  |
| Permit placard or record of permit pulled for last major install | ☐ | ☐ | ☐ |  |
| Equipment labeled with last service date | ☐ | ☐ | ☐ |  |
| No field modifications that appear to bypass safety controls | ☐ | ☐ | ☐ |  |
| Equipment suitable for fuel type and application installed | ☐ | ☐ | ☐ |  |

📊  SECTION 11 — SYSTEM PERFORMANCE & AGE SUMMARY

Equipment Age & Condition Summary

| System / Component | Age (yrs) | Expected Life | Condition Rating | Repair Est. | Replace Est. |
| --- | --- | --- | --- | --- | --- |
| Furnace / Air Handler | ______ | ______ | ✅ ☐ ⚠️ ☐ ⛔ ☐ | $__________ | $__________ |
| Air Conditioner / Heat Pump (Outdoor) | ______ | ______ | ✅ ☐ ⚠️ ☐ ⛔ ☐ | $__________ | $__________ |
| Ductwork System | ______ | ______ | ✅ ☐ ⚠️ ☐ ⛔ ☐ | $__________ | $__________ |
| Thermostat / Controls | ______ | ______ | ✅ ☐ ⚠️ ☐ ⛔ ☐ | $__________ | $__________ |
| Water Heater (if HVAC-related) | ______ | ______ | ✅ ☐ ⚠️ ☐ ⛔ ☐ | $__________ | $__________ |
| Ventilation / Exhaust Fans | ______ | ______ | ✅ ☐ ⚠️ ☐ ⛔ ☐ | $__________ | $__________ |
| Humidifier / Dehumidifier | ______ | ______ | ✅ ☐ ⚠️ ☐ ⛔ ☐ | $__________ | $__________ |
| Air Filtration / UV / IAQ | ______ | ______ | ✅ ☐ ⚠️ ☐ ⛔ ☐ | $__________ | $__________ |

Expected Useful Life Reference (Industry Guidelines)

| Equipment | Avg. Life | Max Life | Notes |
| --- | --- | --- | --- |
| Gas Furnace | 18 yrs | 25 yrs | Heat exchanger failure most common end-of-life cause |
| Central A/C (split) | 15 yrs | 20 yrs | R-22 units: parts increasingly unavailable |
| Heat Pump | 14 yrs | 18 yrs | Higher cycle count due to year-round use |
| Air Handler (fan coil) | 20 yrs | 25 yrs | Motor and coil condition are key factors |
| Ductwork | 25 yrs | 50 yrs | Flex duct degrades faster; metal long-lasting if sealed |
| Thermostat | 10 yrs | 15 yrs | Smart thermostats: firmware/support lifespan shorter |
| Humidifier | 10 yrs | 15 yrs | Water panel / drum requires annual replacement |

📝  SECTION 12 — DEFICIENCIES & RECOMMENDATIONS

Identified Deficiencies Log

| # | Deficiency / Item Noted | System / Location | Rating | Recommended Action | Est. Cost |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  | ✅ ☐ ⚠️ ☐ ⛔ ☐ | ☐ Repair ☐ Replace ☐ Monitor | $__________ |
| 2 |  |  | ✅ ☐ ⚠️ ☐ ⛔ ☐ | ☐ Repair ☐ Replace ☐ Monitor | $__________ |
| 3 |  |  | ✅ ☐ ⚠️ ☐ ⛔ ☐ | ☐ Repair ☐ Replace ☐ Monitor | $__________ |
| 4 |  |  | ✅ ☐ ⚠️ ☐ ⛔ ☐ | ☐ Repair ☐ Replace ☐ Monitor | $__________ |
| 5 |  |  | ✅ ☐ ⚠️ ☐ ⛔ ☐ | ☐ Repair ☐ Replace ☐ Monitor | $__________ |
| 6 |  |  | ✅ ☐ ⚠️ ☐ ⛔ ☐ | ☐ Repair ☐ Replace ☐ Monitor | $__________ |
| 7 |  |  | ✅ ☐ ⚠️ ☐ ⛔ ☐ | ☐ Repair ☐ Replace ☐ Monitor | $__________ |
| 8 |  |  | ✅ ☐ ⚠️ ☐ ⛔ ☐ | ☐ Repair ☐ Replace ☐ Monitor | $__________ |

Priority Action Summary

⛔ Items Requiring Immediate Attention (Safety or Major Function):

⚠️ Items to Address Within 1–2 Years (Monitor / Plan):

✅ Recommended Maintenance Actions (Routine):

💬  SECTION 13 — INSPECTOR COMMENTS & NARRATIVE

Overall System Narrative

Limitations & Conditions of Inspection

Systems Not Tested (reason): ☐ Heating – outdoor temp >65°F ☐ Cooling – outdoor temp <60°F ☐ Power off ☐ Other:

Access Limitations: ☐ None ☐ Attic inaccessible ☐ Crawl inaccessible ☐ Panels locked ☐ Other:

Inspection Scope: Visual, non-invasive inspection. Not a replacement for specialist HVAC inspection or load calculation.

✅  SECTION 14 — OVERALL HVAC SYSTEM RATING

Overall HVAC System Rating: ✅ Acceptable – system operational, minor maintenance noted ☐ ⚠️ Monitor – aging equipment or deficiencies present, plan for repairs ☐ ⛔ Deficient – major repair or replacement recommended before closing ☐

Heating System Status: ✅ Operational ☐ ⚠️ Marginal ☐ ⛔ Failed / Unsafe ☐ N/A ☐

Cooling System Status: ✅ Operational ☐ ⚠️ Marginal ☐ ⛔ Failed / Unsafe ☐ N/A ☐

Duct System Status: ✅ Acceptable ☐ ⚠️ Leaky / Damaged ☐ ⛔ Major Issues ☐ N/A ☐

IAQ / Ventilation Status: ✅ Acceptable ☐ ⚠️ Needs Improvement ☐ ⛔ Health Concern ☐ N/A ☐

Estimated Total Repair Cost: $__________

Estimated Equipment Replacement Cost (if recommended): $__________

Further Specialist Inspection Recommended: ☐ Yes — Specify: ________________________ ☐ No

✍️  SECTION 15 — AUTHORIZATION & SIGNATURES

By signing below, the inspector certifies this report reflects their professional observations at the time of inspection. The client acknowledges receipt, understands the scope limitations, and has had the opportunity to ask questions. This report does not constitute a warranty of any HVAC system or component.

| INSPECTOR / TECHNICIAN SIGNATURE Signature / Date | HOMEOWNER / CLIENT SIGNATURE Signature / Date |
| --- | --- |

| Print Name (Inspector): ________________________ | Print Name (Client): ________________________ |
| --- | --- |
| Company / License #: ________________________ | Date Signed: ________________________ |
| Report Delivered Via: ☐ Email ☐ Print ☐ Portal | Client Copy Received: ☐ Yes ☐ No |

🗂️  SECTION 16 — OFFICE USE ONLY

| Report Entered By: ________________________ | Date Filed: ________________________ |
| --- | --- |
| Report # Assigned: ________________________ | Invoice #: ________________________ |
| Follow-Up Quote Generated: ☐ Yes Quote #: ________ ☐ No | Work Scheduled: ☐ Yes WO #: ________ ☐ No |
| Digital Report Sent: ☐ Yes ☐ No Date: ____________ | Customer Portal Updated: ☐ Yes ☐ No ☐ N/A |