HVAC SAFETY INSPECTION CHECKLIST Complete all applicable sections. Hazards rated: ⛔ Critical ⚠️ Caution ✅ Acceptable. Tag-Out equipment if Critical hazard found.

| ⛔ CRITICAL Tag-Out / Do Not Operate — immediate repair required | ⚠️ CAUTION Deficiency noted — repair at next opportunity | ✅ ACCEPTABLE Within safe operating parameters |
| --- | --- | --- |

📋  SECTION 1 — JOB SITE & TECHNICIAN INFORMATION

| Safety Check #: ________________________ | Date: ________________________ |
| --- | --- |
| Technician Name: ________________________ | Cert # / License #: ________________________ |
| Supervisor / Lead: ________________________ | Company: ________________________ |
| Customer Name: ________________________ | Phone: ________________________ |
| Job Site Address: ________________________ | City / State / ZIP: ________________________ |
| Work Order #: ________________________ | Job Type: ☐ Service ☐ Install ☐ Inspection |
| Work Scope: ________________________ | Ambient Temp: ______°F Humidity: _____%RH |
| Time Work Started: ________________________ | Time Completed: ________________________ |

🔍  SECTION 2 — PRE-WORK SITE SAFETY ASSESSMENT

Site Conditions

| Site Condition / Hazard | ⛔ Critical | ⚠️ Caution | ✅ OK | Notes / Action Required |
| --- | --- | --- | --- | --- |
| Access & Egress |  |  |  |  |
| Clear, unobstructed access to all equipment verified | ☐ | ☐ | ☐ |  |
| Emergency exit routes identified and unobstructed | ☐ | ☐ | ☐ |  |
| Adequate lighting at all work areas (min. 50 fc task lighting) | ☐ | ☐ | ☐ |  |
| Floor surfaces – dry, no slip/trip hazards in work path | ☐ | ☐ | ☐ |  |
| Roof access – hatch / ladder in safe condition, no ice or debris | ☐ | ☐ | ☐ |  |
| Work Area Clearances |  |  |  |  |
| Equipment service clearances meet code (30" x 36" min. NEC 110.26) | ☐ | ☐ | ☐ |  |
| Overhead hazards assessed (hot pipes, energized parts, falling objects) | ☐ | ☐ | ☐ |  |
| Confined space identified – permit required if applicable | ☐ | ☐ | ☐ |  |
| Adjacent equipment / occupants notified of planned work | ☐ | ☐ | ☐ |  |
| Environmental |  |  |  |  |
| Asbestos / lead paint – no disturbance planned, MSDS available | ☐ | ☐ | ☐ |  |
| Mold suspected – proper PPE donned, remediation protocol followed | ☐ | ☐ | ☐ |  |
| Standing water / flooding – electrical equipment de-energized before entry | ☐ | ☐ | ☐ |  |
| Temperature extremes (heat/cold stress protocols activated if applicable) | ☐ | ☐ | ☐ |  |

🦺  SECTION 3 — PERSONAL PROTECTIVE EQUIPMENT (PPE)

PPE Required & Inspection Status

| PPE Item | Required For | ☐ On Person | ☐ Inspected OK |
| --- | --- | --- | --- |
| Safety glasses / goggles | All tasks | ☐ | ☐ |
| Insulated rubber gloves (class per voltage) | Electrical work | ☐ | ☐ |
| Arc flash rated PPE (HRC level: ____) | High-voltage / panel work | ☐ | ☐ |
| Hard hat / bump cap | Rooftop / overhead work | ☐ | ☐ |
| Steel-toed boots | All job sites | ☐ | ☐ |
| Knee pads | Crawl space / tight access | ☐ | ☐ |
| Hearing protection (if >85 dBA) | Mechanical rooms | ☐ | ☐ |
| Respirator / N95 (mold, refrigerant, dust) | Coil cleaning, attic work | ☐ | ☐ |
| Fall protection harness (> 6 ft elevation) | Rooftop, lift, ladder | ☐ | ☐ |
| High-visibility vest | Parking lots, active traffic areas | ☐ | ☐ |
| Chemical-resistant gloves (refrigerant handling) | Refrigerant recovery/charging | ☐ | ☐ |
| Face shield | Refrigerant, chemical, or arc flash tasks | ☐ | ☐ |

Tool Inspection Note:  All hand tools, power tools, and test equipment inspected before use. Damaged tools removed from service.

🔒  SECTION 4 — LOCKOUT / TAGOUT (LOTO) PROCEDURE

| LOTO Required: ☐ Yes — complete table below ☐ No — justify: | LOTO Program Reference #: ________________________ |
| --- | --- |
| Energy Sources Present: ☐ 120/240V ☐ 3-Phase ☐ Natural Gas ☐ Refrigerant ☐ Stored Mech. | LOTO Performed By: ________________________ |
| Lockout Device Used: ☐ Hasp ☐ Personal Lock ☐ Group Lock Box ☐ Tag Only | Lock Serial #: ________________________ |
| Zero-Energy Verified By: ________________________ | Verification Method: ☐ Meter ☐ Test Lamp ☐ Visual |

LOTO Sequence Log

| Step | LOTO Procedure Step | Completed By | Time | Verified By |
| --- | --- | --- | --- | --- |
| 1 | Notify all affected personnel of planned shutdown |  |  |  |
| 2 | Identify all energy sources (electrical, gas, refrigerant pressure, stored mechanical) |  |  |  |
| 3 | Shut down equipment using normal stopping procedure |  |  |  |
| 4 | Open / de-energize all disconnects and isolation valves |  |  |  |
| 5 | Apply lockout devices to each energy-isolating device |  |  |  |
| 6 | Apply personal danger tag to each lockout device |  |  |  |
| 7 | Release / restrain all stored energy (bleed pressure, discharge capacitors) |  |  |  |
| 8 | Verify zero energy state — test at equipment terminals before working |  |  |  |
| 9 | Perform maintenance / inspection |  |  |  |
| 10 | Remove LOTO in reverse order — confirm all personnel are clear before re-energizing |  |  |  |

⚡  SECTION 5 — ELECTRICAL SAFETY

| Electrical Safety Check Item | ⛔ Critical | ⚠️ Caution | ✅ OK | Notes / Action Required |
| --- | --- | --- | --- | --- |
| Service & Disconnects |  |  |  |  |
| Main disconnect / OCPD – accessible, labeled, correct amperage | ☐ | ☐ | ☐ |  |
| Disconnect enclosure – no missing knockouts, cover secured | ☐ | ☐ | ☐ |  |
| No double-tapped breakers or fuses of incorrect rating | ☐ | ☐ | ☐ |  |
| Arc flash label present and legible on panels / MCCs | ☐ | ☐ | ☐ |  |
| Wiring & Connections |  |  |  |  |
| No exposed conductors, damaged insulation, or burnt wiring | ☐ | ☐ | ☐ |  |
| All wire connections tight – no overheating evidence (thermography or touch test) | ☐ | ☐ | ☐ |  |
| Grounding / bonding conductors present and intact | ☐ | ☐ | ☐ |  |
| Ground fault protection (GFCI) – tested and operational where required | ☐ | ☐ | ☐ |  |
| Neutral / ground not bonded downstream of main service | ☐ | ☐ | ☐ |  |
| Work Practice |  |  |  |  |
| Energized work permit obtained if live work unavoidable | ☐ | ☐ | ☐ |  |
| Minimum approach distance maintained for voltage class | ☐ | ☐ | ☐ |  |
| Only qualified person performing electrical tasks | ☐ | ☐ | ☐ |  |
| Insulated tools used on or near energized parts | ☐ | ☐ | ☐ |  |
| Capacitors discharged before handling (min. 5 minutes after shutoff) | ☐ | ☐ | ☐ |  |
| Temporary Power & Cords |  |  |  |  |
| Extension cords – 3-prong, correct gauge, no splices or tape repairs | ☐ | ☐ | ☐ |  |
| Temporary power source – GFCI protected | ☐ | ☐ | ☐ |  |
| No cords run under doors, through walls, or across walkways unprotected | ☐ | ☐ | ☐ |  |

🔥  SECTION 6 — GAS & COMBUSTION SAFETY

| Gas & Combustion Safety Item | ⛔ Critical | ⚠️ Caution | ✅ OK | Notes / Action Required |
| --- | --- | --- | --- | --- |
| Gas Supply |  |  |  |  |
| Gas shutoff valve – accessible, labeled, operational | ☐ | ☐ | ☐ |  |
| Gas lines – no visible corrosion, improper supports, or mechanical damage | ☐ | ☐ | ☐ |  |
| Gas leak check performed (soap test or electronic sniffer) | ☐ | ☐ | ☐ |  |
| CO detector / gas detector – present, tested, in calibration date | ☐ | ☐ | ☐ |  |
| Combustion Equipment |  |  |  |  |
| Furnace / boiler – no cracks in heat exchanger (CO test negative) | ☐ | ☐ | ☐ |  |
| Flue / vent pipe – intact, sloped correctly, no blockage or backdraft | ☐ | ☐ | ☐ |  |
| Combustion air openings – unobstructed, correct free area per code | ☐ | ☐ | ☐ |  |
| Draft test performed – natural draft appliance not backdrafting | ☐ | ☐ | ☐ |  |
| Burner flames – correct color (blue), no yellow tips, no rollout | ☐ | ☐ | ☐ |  |
| CO Safety |  |  |  |  |
| Ambient CO measured at return air grille: ______ ppm (limit: <35 ppm action level) | ☐ | ☐ | ☐ |  |
| CO at flue measured: ______ ppm (limit: <400 ppm undiluted) | ☐ | ☐ | ☐ |  |
| No combustion appliance spillage detected | ☐ | ☐ | ☐ |  |
| CO alarm installed within 15 ft of combustion appliance (per IRC R315) | ☐ | ☐ | ☐ |  |

❄️  SECTION 7 — REFRIGERANT & CHEMICAL SAFETY

| Refrigerant & Chemical Safety Item | ⛔ Critical | ⚠️ Caution | ✅ OK | Notes / Action Required |
| --- | --- | --- | --- | --- |
| Regulatory Compliance |  |  |  |  |
| Technician holds valid EPA 608 certification (Universal or applicable type) | ☐ | ☐ | ☐ |  |
| Refrigerant type and GWP documented on service record | ☐ | ☐ | ☐ |  |
| Refrigerant log maintained per EPA Section 608 requirements | ☐ | ☐ | ☐ |  |
| No intentional venting of refrigerant — recovery equipment on site | ☐ | ☐ | ☐ |  |
| Handling & Storage |  |  |  |  |
| Refrigerant cylinders – upright, secured, valve caps on, not overfilled | ☐ | ☐ | ☐ |  |
| Cylinders stored away from heat sources and direct sunlight | ☐ | ☐ | ☐ |  |
| Recovery cylinder within hydrostatic test date (≤5 years for DOT) | ☐ | ☐ | ☐ |  |
| Recovery machine in working order, filter drier serviceable | ☐ | ☐ | ☐ |  |
| SDS / Safety Data Sheet available for all refrigerants and chemicals on site | ☐ | ☐ | ☐ |  |
| Leak Response |  |  |  |  |
| Refrigerant leak detector – calibrated, operational | ☐ | ☐ | ☐ |  |
| No refrigerant odor or visible frost indicating active leak in occupied space | ☐ | ☐ | ☐ |  |
| Ventilation adequate in mechanical room (ASHRAE 15 oxygen depletion alarm if required) | ☐ | ☐ | ☐ |  |
| Chemical spill kit present (coil cleaners, flux, solvents) | ☐ | ☐ | ☐ |  |
| Coil Cleaning Chemicals |  |  |  |  |
| Chemical label read – application method and PPE followed | ☐ | ☐ | ☐ |  |
| Neutralizer / rinse water – disposed of properly, not down storm drain | ☐ | ☐ | ☐ |  |

🏗️  SECTION 8 — FALL PROTECTION & ROOFTOP / ELEVATED WORK

| Fall Protection & Elevated Work Item | ⛔ Critical | ⚠️ Caution | ✅ OK | Notes / Action Required |
| --- | --- | --- | --- | --- |
| Rooftop Access |  |  |  |  |
| Roof access authorized by facility owner / property manager | ☐ | ☐ | ☐ |  |
| Roof condition assessed – no soft spots, ponding water, or ice | ☐ | ☐ | ☐ |  |
| Roof edge / skylight – guardrails present or warning line system established | ☐ | ☐ | ☐ |  |
| Leading edge work >6 ft – fall arrest system in use | ☐ | ☐ | ☐ |  |
| Personal Fall Arrest System (PFAS) |  |  |  |  |
| Full-body harness – donned, all D-rings and webbing inspected | ☐ | ☐ | ☐ |  |
| Lanyard / SRL – connected to certified anchorage point (5,000 lb min.) | ☐ | ☐ | ☐ |  |
| Anchorage point – rated, inspected, documentation available | ☐ | ☐ | ☐ |  |
| Rescue plan – discussed with crew before elevated work begins | ☐ | ☐ | ☐ |  |
| Ladders |  |  |  |  |
| Ladder type correct for task (Type IA or I for commercial use) | ☐ | ☐ | ☐ |  |
| Ladder set at 4:1 angle, feet secured, top tied off or stabilized | ☐ | ☐ | ☐ |  |
| Three points of contact maintained at all times | ☐ | ☐ | ☐ |  |
| Ladder free of grease, oil, and damage | ☐ | ☐ | ☐ |  |
| Extension ladder extends 3 ft above roofline / landing | ☐ | ☐ | ☐ |  |
| Aerial Work Platforms / Lifts |  |  |  |  |
| Operator trained and authorized for equipment type | ☐ | ☐ | ☐ |  |
| Pre-operation inspection completed (tires, controls, safety devices) | ☐ | ☐ | ☐ |  |
| Outriggers / stabilizers deployed on firm, level ground | ☐ | ☐ | ☐ |  |
| Overhead power lines – minimum 10 ft clearance (>50kV: additional) | ☐ | ☐ | ☐ |  |

🚧  SECTION 9 — CONFINED SPACE ENTRY

| Confined Space Present: ☐ Yes — complete section ☐ No — skip to Section 10 |
| --- |
| Space Classification: ☐ Non-Permit Required ☐ Permit-Required | Permit #: ________________________ |
| Entry Supervisor: ________________________ | Attendant (Outside): ________________________ |
| Atmospheric Test – O₂: ______% (normal: 19.5–23.5%) | Combustible Gas: ______% LEL (action: >10%) |
| Atmospheric Test – CO: ______ ppm (limit: 35 ppm TWA) | H₂S: ______ ppm (limit: 10 ppm TWA) |
| Ventilation Provided: ☐ Yes ☐ No Type: ____________________ | Rescue Equipment On Site: ☐ Yes ☐ No |

| Confined Space Safety Item | ⛔ Critical | ⚠️ Caution | ✅ OK | Notes / Action Required |
| --- | --- | --- | --- | --- |
| Entry permit completed and posted at entry point | ☐ | ☐ | ☐ |  |
| Atmospheric testing performed before and continuously during entry | ☐ | ☐ | ☐ |  |
| Attendant stationed at entry — communication maintained at all times | ☐ | ☐ | ☐ |  |
| Retrieval / rescue equipment positioned at entry (tripod, lifeline, SCBA) | ☐ | ☐ | ☐ |  |
| All entrants logged in and out | ☐ | ☐ | ☐ |  |
| Emergency services / rescue team on standby (permit-required spaces) | ☐ | ☐ | ☐ |  |

🚒  SECTION 10 — FIRE PREVENTION & EMERGENCY PREPAREDNESS

| Fire & Emergency Safety Item | ⛔ Critical | ⚠️ Caution | ✅ OK | Notes / Action Required |
| --- | --- | --- | --- | --- |
| Fire Prevention |  |  |  |  |
| Hot work permit obtained if brazing / soldering required | ☐ | ☐ | ☐ |  |
| Fire extinguisher on site – ABC rated, charged, within annual inspection date | ☐ | ☐ | ☐ |  |
| Fire watch stationed during and 30 minutes post hot work | ☐ | ☐ | ☐ |  |
| Combustibles cleared 35 ft radius from hot work area | ☐ | ☐ | ☐ |  |
| Flame-resistant tarp / welding blanket protecting adjacent surfaces | ☐ | ☐ | ☐ |  |
| Smoke / fire detectors in work area – temporarily covered (uncovered immediately after work) | ☐ | ☐ | ☐ |  |
| Emergency Preparedness |  |  |  |  |
| Emergency contact numbers posted / saved: facility, emergency services, supervisor | ☐ | ☐ | ☐ |  |
| First aid kit location identified | ☐ | ☐ | ☐ |  |
| AED location identified (if available on site) | ☐ | ☐ | ☐ |  |
| Emergency gas shutoff location confirmed with facility contact | ☐ | ☐ | ☐ |  |
| Emergency electrical shutoff location confirmed | ☐ | ☐ | ☐ |  |
| Evacuation muster point identified | ☐ | ☐ | ☐ |  |
| Incident Reporting |  |  |  |  |
| All near-misses and incidents to be reported to supervisor immediately | ☐ | ☐ | ☐ |  |
| Incident report form available (company) | ☐ | ☐ | ☐ |  |
| OSHA recordable criteria understood by technician | ☐ | ☐ | ☐ |  |

🚐  SECTION 11 — VEHICLE, MATERIAL HANDLING & TOOL SAFETY

| Vehicle, Material & Tool Safety Item | ⛔ Critical | ⚠️ Caution | ✅ OK | Notes / Action Required |
| --- | --- | --- | --- | --- |
| Service Vehicle |  |  |  |  |
| Vehicle daily inspection completed (tires, lights, fluid levels) | ☐ | ☐ | ☐ |  |
| Cargo secured – no loose equipment or cylinders unsecured in van | ☐ | ☐ | ☐ |  |
| Vehicle parked safely – cones / safety triangles deployed if in traffic | ☐ | ☐ | ☐ |  |
| DOT placards displayed if carrying HAZMAT (refrigerant > threshold) | ☐ | ☐ | ☐ |  |
| Manual Material Handling |  |  |  |  |
| Loads >50 lbs – two-person lift or mechanical assist used | ☐ | ☐ | ☐ |  |
| Proper lift technique used (back straight, legs, close to body) | ☐ | ☐ | ☐ |  |
| Hand truck / dolly used for heavy equipment (condenser, AHU, cylinders) | ☐ | ☐ | ☐ |  |
| Cutting / sharp sheet metal – gloves worn, edges de-burred | ☐ | ☐ | ☐ |  |
| Power & Hand Tools |  |  |  |  |
| Grinder – wheel rated for RPM, guard in place, face shield worn | ☐ | ☐ | ☐ |  |
| Drill / rotary tool – chuck key removed before starting | ☐ | ☐ | ☐ |  |
| Reciprocating saw – blade inspected, no contact hazards identified | ☐ | ☐ | ☐ |  |
| Torches – tip cleaned, hoses inspected, flashback arrestors installed | ☐ | ☐ | ☐ |  |
| Vacuum pump – oil level checked, exhaust directed away from personnel | ☐ | ☐ | ☐ |  |

📝  SECTION 12 — IDENTIFIED HAZARDS & CORRECTIVE ACTIONS

Hazard / Finding Log

| # | Hazard / Finding Description | Rating | Action Taken | Resolved By / Date |
| --- | --- | --- | --- | --- |
| 1 |  | ⛔ Crit ⚠️ Caut ✅ OK | ☐ Tagged ☐ Repaired ☐ Monitored |  |
| 2 |  | ⛔ Crit ⚠️ Caut ✅ OK | ☐ Tagged ☐ Repaired ☐ Monitored |  |
| 3 |  | ⛔ Crit ⚠️ Caut ✅ OK | ☐ Tagged ☐ Repaired ☐ Monitored |  |
| 4 |  | ⛔ Crit ⚠️ Caut ✅ OK | ☐ Tagged ☐ Repaired ☐ Monitored |  |
| 5 |  | ⛔ Crit ⚠️ Caut ✅ OK | ☐ Tagged ☐ Repaired ☐ Monitored |  |
| 6 |  | ⛔ Crit ⚠️ Caut ✅ OK | ☐ Tagged ☐ Repaired ☐ Monitored |  |

Additional Safety Notes

✅  SECTION 13 — OVERALL SAFETY STATUS & DISPOSITION

Overall Job-Site Safety Rating: ⛔ CRITICAL — Work stopped, tagged, supervisor notified ☐ ⚠️ CAUTION — Deficiencies noted, repair scheduled ☐ ✅ ACCEPTABLE — All items satisfactory ☐

Equipment Tagged Out: ☐ Yes — Tag # / Location: ________________________ ☐ No

Work Stopped / Customer Notified: ☐ Yes — Reason: ________________________ ☐ No

Follow-Up Required: ☐ Yes — Scheduled: ________________________ ☐ No

Regulatory Authority Notification Required: ☐ Yes — Agency: ________________________ ☐ No ☐ TBD

✍️  SECTION 14 — AUTHORIZATION & SIGNATURES

By signing below, all parties confirm this safety checklist was completed to the best of their knowledge, all identified hazards were communicated, and appropriate corrective actions were initiated. Technician certifies compliance with company safety policies and applicable OSHA standards.

| TECHNICIAN SIGNATURE Signature / Date | SUPERVISOR / LEAD SIGNATURE Signature / Date | CUSTOMER / OWNER SIGNATURE Signature / Date |
| --- | --- | --- |

| Print Name (Technician): ______________________ | Print Name (Supervisor): ______________________ | Print Name (Customer): ______________________ |
| --- | --- | --- |
| Certifications (EPA 608 / NATE): ______________________ | Date Signed: ______________________ | Date Signed: ______________________ |

🗂️  SECTION 15 — OFFICE USE ONLY

| Received By: ________________________ | Date Filed: ________________________ |
| --- | --- |
| Safety Incident Report Filed: ☐ Yes Report #: ________ ☐ No | OSHA Recordable: ☐ Yes ☐ No ☐ TBD |
| Work Order Updated: ☐ Yes ☐ No WO #: ____________ | Follow-Up WO Created: ☐ Yes WO #: ________ ☐ No |
| Customer Copy Provided: ☐ Yes ☐ No | Digital Record Saved: ☐ Yes ☐ No |