HVAC ROUGH-IN INSPECTION CHECKLIST New Construction & Major Renovation — Mechanical Rough-In Phase

| PROJECT INFORMATION |  |  |  |
| --- | --- | --- | --- |
| Project Name: | ________________________________ | Job #: | ____________ |
| Site Address: | ________________________________ | Date: | ____________ |
| General Contractor: | ________________________ | Permit #: | ____________ |
| HVAC Contractor: | __________________________ | Inspector: | ____________ |
| System Type: | ________________________________ | Phase: | ____________ |
| Inspection Stage: | Rough-In | Weather: | ____________ |

🪟  SECTION 1 — DUCTWORK & AIR DISTRIBUTION

| # | Inspection Item / Description | Pass | Fail | N/A | Notes / Corrective Action |
| --- | --- | --- | --- | --- | --- |
| 1 | Duct layout matches approved mechanical drawings and specifications | ☐ | ☐ | ☐ |  |
| 2 | All supply and return duct sizes conform to design CFM requirements | ☐ | ☐ | ☐ |  |
| 3 | Flexible duct connections properly supported — max 4 ft unsupported runs | ☐ | ☐ | ☐ |  |
| 4 | All rigid duct joints sealed with UL-181 mastic or approved foil tape (no duct tape) | ☐ | ☐ | ☐ |  |
| 5 | Duct penetrations through fire-rated assemblies have approved fire dampers installed | ☐ | ☐ | ☐ |  |
| 6 | Return air plenums properly isolated — no combustion air contamination pathway | ☐ | ☐ | ☐ |  |
| 7 | Duct chase or shaft dimensions match drawings; no obstructions to future access | ☐ | ☐ | ☐ |  |
| 8 | Supply diffuser / grille rough-in openings correct size, location, and framing | ☐ | ☐ | ☐ |  |
| 9 | Return air grille rough-in openings correct size, location, and framing | ☐ | ☐ | ☐ |  |
| 10 | All flex duct installed with minimum bends; no kinks or crushed sections | ☐ | ☐ | ☐ |  |
| 11 | Duct hangers and supports meet SMACNA spacing requirements (max 10 ft rigid) | ☐ | ☐ | ☐ |  |
| 12 | Exterior wall supply ducts include vapor barrier or insulation to prevent condensation | ☐ | ☐ | ☐ |  |
| 13 | Transfer grilles or jumper ducts installed per room pressure relief design | ☐ | ☐ | ☐ |  |

Duct Leakage Test Data (Pre-Insulation)

| Parameter | Design / Spec | Measured | Unit | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| Total Duct Leakage (CFM25) | ≤ 4 CFM25/100 sq ft | ______ | ______ | ______ |  |
| Leakage to Outside (CFM25) | ≤ 2 CFM25/100 sq ft | ______ | ______ | ______ |  |
| Test Pressure | 25 Pa | ______ | ______ | ______ |  |
| Conditioned Floor Area | ________ sq ft | ______ | ______ | ______ |  |
| Pass/Fail Threshold CFM25 | ________ | ______ | ______ | ______ |  |

🔧  SECTION 2 — EQUIPMENT ROUGH-IN & CLEARANCES

| # | Inspection Item / Description | Pass | Fail | N/A | Notes / Corrective Action |
| --- | --- | --- | --- | --- | --- |
| 1 | Air handler / furnace unit platform or curb correctly sized and level | ☐ | ☐ | ☐ |  |
| 2 | Equipment clearances meet manufacturer specs (front service, sides, top) | ☐ | ☐ | ☐ |  |
| 3 | Combustion air openings sized per NFPA 54 / local code — unobstructed | ☐ | ☐ | ☐ |  |
| 4 | Gas line rough-in correct size, location, and CSST bonding per code | ☐ | ☐ | ☐ |  |
| 5 | Flue / venting rough-in correct diameter, material (Category I–IV), and pitch | ☐ | ☐ | ☐ |  |
| 6 | Category III/IV venting uses listed sealed stainless or PVC — no galvanized | ☐ | ☐ | ☐ |  |
| 7 | Condensate primary and secondary drain lines installed with proper slope (1/4" per ft) | ☐ | ☐ | ☐ |  |
| 8 | Condensate overflow pan installed under attic/second-floor air handlers | ☐ | ☐ | ☐ |  |
| 9 | Refrigerant line sets correctly sized (suction/liquid), routed, and supported | ☐ | ☐ | ☐ |  |
| 10 | Refrigerant line set penetrations sleeved and sealed against air/pest infiltration | ☐ | ☐ | ☐ |  |
| 11 | Electrical disconnect locations meet NEC 110.26 clearance requirements | ☐ | ☐ | ☐ |  |
| 12 | Unit mounting pads (exterior condensers) level, correctly sized, and isolated from structure | ☐ | ☐ | ☐ |  |
| 13 | Rooftop unit curbs properly flashed and sealed; curb height meets membrane requirements | ☐ | ☐ | ☐ |  |
| 14 | Makeup air unit rough-in (if applicable) matches ventilation schedule | ☐ | ☐ | ☐ |  |

💧  SECTION 3 — HYDRONIC & REFRIGERANT PIPING

| # | Inspection Item / Description | Pass | Fail | N/A | Notes / Corrective Action |
| --- | --- | --- | --- | --- | --- |
| 1 | Hydronic pipe sizing matches design documents (supply/return header sizes) | ☐ | ☐ | ☐ |  |
| 2 | Pipe material correct per specification (Type L copper, black steel, PEX, etc.) | ☐ | ☐ | ☐ |  |
| 3 | All solder joints properly cleaned, fluxed, and completed — no cold joints visible | ☐ | ☐ | ☐ |  |
| 4 | Hydronic piping slope correct for air venting: 1" per 10 ft minimum toward vents | ☐ | ☐ | ☐ |  |
| 5 | Air separators and expansion tank rough-in locations match design drawings | ☐ | ☐ | ☐ |  |
| 6 | Pipe hangers and supports per MSS SP-58; correct spacing for pipe size and material | ☐ | ☐ | ☐ |  |
| 7 | Refrigerant copper line sets correct OD for system tonnage (per Manufacturer Table) | ☐ | ☐ | ☐ |  |
| 8 | Refrigerant line insulation: suction line fully insulated, no gaps at supports | ☐ | ☐ | ☐ |  |
| 9 | No refrigerant lines in direct contact with structure or other pipes (vibration isolation) | ☐ | ☐ | ☐ |  |
| 10 | Condensate drain lines: correct pipe size, slope, trap depth, and cleanout access | ☐ | ☐ | ☐ |  |
| 11 | Pressure test completed and documented (see test data table below) | ☐ | ☐ | ☐ |  |
| 12 | Dielectric unions installed at dissimilar metal connections | ☐ | ☐ | ☐ |  |

Pressure Test Record

| Parameter | Design / Spec | Measured | Unit | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| Test Medium | Nitrogen (Refrigerant) / Water (Hydronic) | ______ | ______ | ______ |  |
| Test Pressure (PSIG) | ________ PSIG | ______ | ______ | ______ |  |
| Hold Duration | ________ minutes | ______ | ______ | ______ |  |
| Start Pressure | ________ PSIG | ______ | ______ | ______ |  |
| End Pressure | ________ PSIG | ______ | ______ | ______ |  |
| Pressure Drop (allowable ≤ 0) | ________ PSIG | ______ | ______ | ______ |  |
| Test Date / Technician | ________________ | ______ | ______ | ______ |  |

⚡  SECTION 4 — ELECTRICAL ROUGH-IN

| # | Inspection Item / Description | Pass | Fail | N/A | Notes / Corrective Action |
| --- | --- | --- | --- | --- | --- |
| 1 | Electrical panel / sub-panel location and size per mechanical schedule | ☐ | ☐ | ☐ |  |
| 2 | Circuit breaker sizes match equipment nameplate MCA (Minimum Circuit Ampacity) | ☐ | ☐ | ☐ |  |
| 3 | Wire gauge matches breaker size and run length (voltage drop ≤ 3% per NEC) | ☐ | ☐ | ☐ |  |
| 4 | Low-voltage thermostat wiring: correct wire count and gauge per system type | ☐ | ☐ | ☐ |  |
| 5 | 24V control wiring run in conduit or routed away from line-voltage wiring | ☐ | ☐ | ☐ |  |
| 6 | Disconnects lockable and within sight of equipment per NEC 440.14 | ☐ | ☐ | ☐ |  |
| 7 | Grounding conductors properly sized and terminated | ☐ | ☐ | ☐ |  |
| 8 | Junction boxes accessible, not buried in walls without access covers | ☐ | ☐ | ☐ |  |
| 9 | GFI / AFCI protection installed where required by NEC 210.8 | ☐ | ☐ | ☐ |  |
| 10 | VAV controller and BAS/BMS sensor rough-in locations verified against controls design | ☐ | ☐ | ☐ |  |
| 11 | Smoke detector rough-in in supply ductwork (per NFPA 72 and local AHJ) | ☐ | ☐ | ☐ |  |

🌬️  SECTION 5 — VENTILATION, IAQ & CODE COMPLIANCE

| # | Inspection Item / Description | Pass | Fail | N/A | Notes / Corrective Action |
| --- | --- | --- | --- | --- | --- |
| 1 | Outside air intake location: minimum 10 ft from exhaust, contaminant sources | ☐ | ☐ | ☐ |  |
| 2 | OA intake protected with bird/insect screen and rain hood | ☐ | ☐ | ☐ |  |
| 3 | OA quantity meets ASHRAE 62.1 Ventilation Rate Procedure for occupancy type | ☐ | ☐ | ☐ |  |
| 4 | Energy Recovery Ventilator (ERV/HRV) rough-in: intake/exhaust clearances correct | ☐ | ☐ | ☐ |  |
| 5 | Bathroom exhaust fans/ducts routed to exterior (not to attic or unconditioned space) | ☐ | ☐ | ☐ |  |
| 6 | Kitchen exhaust hood duct: correct size, material (26 ga min), and grease clearance | ☐ | ☐ | ☐ |  |
| 7 | Dryer duct: max 25 ft equivalent, smooth metal, no screenings at termination | ☐ | ☐ | ☐ |  |
| 8 | CO/combustion safety detector rough-in locations per local code | ☐ | ☐ | ☐ |  |
| 9 | Economizer rough-in (if applicable) integrated with controls sequence of operations | ☐ | ☐ | ☐ |  |
| 10 | MERV-13 (or specified) filter rack rough-in: correct size, accessible, with gasketing | ☐ | ☐ | ☐ |  |

🧱  SECTION 6 — INSULATION & ENERGY CODE COMPLIANCE

| # | Inspection Item / Description | Pass | Fail | N/A | Notes / Corrective Action |
| --- | --- | --- | --- | --- | --- |
| 1 | Duct insulation type and R-value meets IECC Table C403.2.3 or ASHRAE 90.1 | ☐ | ☐ | ☐ |  |
| 2 | All supply/return ducts in unconditioned spaces insulated: R-8 minimum | ☐ | ☐ | ☐ |  |
| 3 | Duct insulation installed without gaps, tears, or compression at hangers | ☐ | ☐ | ☐ |  |
| 4 | Vapor retarder on insulation: facing installed correctly for climate zone | ☐ | ☐ | ☐ |  |
| 5 | Pipe insulation installed on all hot water and chilled water piping per IECC | ☐ | ☐ | ☐ |  |
| 6 | Equipment installed meets minimum efficiency ratings per IECC (SEER2, HSPF2, AFUE, EER) | ☐ | ☐ | ☐ |  |
| 7 | Energy model equipment schedule matches installed equipment model numbers | ☐ | ☐ | ☐ |  |
| 8 | Demand-controlled ventilation (DCV) controls rough-in verified for applicable spaces | ☐ | ☐ | ☐ |  |

🏠  SECTION 7 — ATTIC, CRAWL SPACE & SPECIAL CONDITIONS

| # | Inspection Item / Description | Pass | Fail | N/A | Notes / Corrective Action |
| --- | --- | --- | --- | --- | --- |
| 1 | Attic air handler platform: minimum 24" high, GFCI receptacle within 25 ft, drain pan | ☐ | ☐ | ☐ |  |
| 2 | Attic walkboard (minimum 24" wide) from access to equipment | ☐ | ☐ | ☐ |  |
| 3 | Attic lighting (bulb or switched outlet) installed at equipment per IRC M1305.1.4.3 | ☐ | ☐ | ☐ |  |
| 4 | Crawl space ducts: minimum clearance maintained, not resting on ground | ☐ | ☐ | ☐ |  |
| 5 | Sealed crawl space: supply or exhaust mechanical ventilation installed | ☐ | ☐ | ☐ |  |
| 6 | Vented crawl space: duct insulation intact, no vapor barrier interruption | ☐ | ☐ | ☐ |  |
| 7 | Underground duct: correct material (Type 1 fiberglass or concrete encased metal) | ☐ | ☐ | ☐ |  |
| 8 | Slab penetrations: pipes sleeved, sealed, and pitched correctly | ☐ | ☐ | ☐ |  |

📋  SECTION 8 — DOCUMENTATION & OUTSTANDING CORRECTIONS

| # | Location / Zone | Deficiency Description | Responsible Party | Re-Inspect Date |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |
| 4 |  |  |  |  |
| 5 |  |  |  |  |
| 6 |  |  |  |  |

| CHECKLIST COMPLETION SUMMARY |  |
| --- | --- |
| Total Items Inspected: | ________ | Items Passing: | ________ |
| Items Failing: | ________ | Items N/A: | ________ |
| Overall Inspection Result: | ☐ PASS ☐ FAIL ☐ CONDITIONAL PASS | Re-Inspection Required: | ☐ Yes ☐ No |
| Conditional Pass Notes: | ________________________________________ | Permit Status: | ________ |

✅  SECTION 9 — APPROVALS & SIGN-OFF

| INSPECTOR SIGN-OFF & AUTHORIZATION |  |  |
| --- | --- | --- |
| HVAC Contractor / Inspector Name: ________________________________ Signature: ___________________________ Company: ____________________________ Date: _______________________________ License #: __________________________ | General Contractor Name: ________________________________ Signature: ___________________________ Company: ____________________________ Date: _______________________________ License #: __________________________ | Owner / Owner's Rep Name: ________________________________ Signature: ___________________________ Company: ____________________________ Date: _______________________________ License #: __________________________ |

CERTIFICATION STATEMENT By signing above, the HVAC Contractor certifies that all work inspected herein has been installed in accordance with the approved construction documents, applicable mechanical codes (IMC/UMC), NFPA 54, ASHRAE 62.1 & 90.1, local amendments, and manufacturer installation instructions. All failing items must be corrected and re-inspected prior to concealment or final approval. This document shall be maintained in the project file and made available to the Authority Having Jurisdiction (AHJ) upon request.