HVAC SEASONAL TUNE-UP CHECKLIST Comprehensive Maintenance, Safety Inspection & Performance Verification

| SERVICE VISIT INFORMATION |  |  |  |
| --- | --- | --- | --- |
| Customer Name: | ________________________________ | Work Order #: | ____________ |
| Service Address: | ________________________________ | Visit Date: | ____________ |
| Contact Phone: | ________________________________ | Arrival Time: | ____________ |
| Equipment Location: | ____________________________ | Departure Time: | ____________ |
| Technician Name: | ______________________________ | License #: | ____________ |
| Equipment Make / Model: | ______________________ | Serial #: | ____________ |
| System Type: | ________________________________ | System Age (yrs): | ____________ |
| Service Agreement #: | ________________________ | Season: | ☐ Cooling ☐ Heating |

PRE-EXISTING CONDITIONS NOTED AT ARRIVAL

Document any conditions found BEFORE work begins to protect both technician and customer: ________________________________________________________________________________ ________________________________________________________________________________ ________________________________________________________________________________ Overall System Condition at Arrival: ☐ Good ☐ Fair ☐ Poor ☐ Critical — Needs Immediate Repair

🔍  SECTION 1 — SAFETY INSPECTION & VISUAL ASSESSMENT

| # | Maintenance Task / Inspection Item | Pass | Fail | N/A | Technician Notes |
| --- | --- | --- | --- | --- | --- |
| 1 | Electrical panel: breaker correctly sized per equipment MCA/MOP — no tripped or double-tapped breakers | ☐ | ☐ | ☐ |  |
| 2 | Disconnect switch: correct ampacity, NEMA rating, lockable, and within sight of equipment | ☐ | ☐ | ☐ |  |
| 3 | All electrical wiring: no chafed insulation, loose terminals, exposed conductors, or rodent damage | ☐ | ☐ | ☐ |  |
| 4 | Outdoor unit: no physical damage, leaning, or corrosion on cabinet or base rail | ☐ | ☐ | ☐ |  |
| 5 | Refrigerant lines: insulation intact — no missing or deteriorated sections at penetrations or supports | ☐ | ☐ | ☐ |  |
| 6 | Visible refrigerant oil staining on lines, coil, or cabinet (indicator of active refrigerant leak) | ☐ | ☐ | ☐ |  |
| 7 | Flue / vent pipe: no rust holes, disconnected joints, missing screws, or improper pitch | ☐ | ☐ | ☐ |  |
| 8 | Combustion air openings: unobstructed and correctly sized per NFPA 54 / local code | ☐ | ☐ | ☐ |  |
| 9 | CO detector present and within manufacturer service life (replace per label date) | ☐ | ☐ | ☐ |  |
| 10 | Gas piping: no corrosion, unsupported spans, or unapproved materials in equipment room | ☐ | ☐ | ☐ |  |
| 11 | Condensate pan and drain: no standing water, biological growth, rust, or overflow staining | ☐ | ☐ | ☐ |  |
| 12 | All access panels in place and securely fastened before any electrical testing | ☐ | ☐ | ☐ |  |

🌬️  SECTION 2 — AIR FILTRATION & INDOOR UNIT

| # | Maintenance Task / Inspection Item | Pass | Fail | N/A | Technician Notes |
| --- | --- | --- | --- | --- | --- |
| 1 | Air filter inspected — document MERV rating, size, and condition; replace if clogged or at interval | ☐ | ☐ | ☐ |  |
| 2 | Filter rack: no air bypass around filter frame — gasket intact and filter seated fully | ☐ | ☐ | ☐ |  |
| 3 | Blower wheel inspected: clean blades, no cracks or balance weights missing | ☐ | ☐ | ☐ |  |
| 4 | Blower motor: lubricate oil-port bearings (if applicable); check for wobble or vibration | ☐ | ☐ | ☐ |  |
| 5 | Blower motor amperage measured and within nameplate FLA | ☐ | ☐ | ☐ |  |
| 6 | Blower motor capacitor tested: within ±6% of rated MFD | ☐ | ☐ | ☐ |  |
| 7 | Evaporator coil inspected: no biological fouling, bent fins, or frost/ice buildup | ☐ | ☐ | ☐ |  |
| 8 | Evaporator coil cleaned if fouled (spray-on coil cleaner; rinse if required per product) | ☐ | ☐ | ☐ |  |
| 9 | Indoor cabinet interior: no rust, loose insulation liner, or debris accumulation | ☐ | ☐ | ☐ |  |
| 10 | Supply and return duct connections at unit: sealed, insulated, and secure — no disconnections | ☐ | ☐ | ☐ |  |
| 11 | Indoor unit drain pan cleaned and drain line flushed with water — confirmed flowing freely | ☐ | ☐ | ☐ |  |
| 12 | Condensate trap (if applicable): water-sealed and not dried out | ☐ | ☐ | ☐ |  |
| 13 | Condensate pump (if installed): float switch triggers pump — pump discharges freely | ☐ | ☐ | ☐ |  |
| 14 | UV light / air purifier (if installed): bulb operational and within replacement interval | ☐ | ☐ | ☐ |  |

🏗️  SECTION 3 — OUTDOOR UNIT INSPECTION & CLEANING

| # | Maintenance Task / Inspection Item | Pass | Fail | N/A | Technician Notes |
| --- | --- | --- | --- | --- | --- |
| 1 | Condenser coil fins inspected: no heavy fouling, cottonwood, mud, or debris blocking face | ☐ | ☐ | ☐ |  |
| 2 | Condenser coil cleaned with coil cleaner or low-pressure water rinse — rinsed clean | ☐ | ☐ | ☐ |  |
| 3 | Coil fins straightened with fin comb where bent (document % obstruction before/after) | ☐ | ☐ | ☐ |  |
| 4 | Condenser fan blade: no cracks, bends, or missing balance weights; rotates freely by hand | ☐ | ☐ | ☐ |  |
| 5 | Condenser fan motor: lubricate oil-port bearings (if applicable); no wobble or rattling | ☐ | ☐ | ☐ |  |
| 6 | Condenser fan motor amperage measured and within nameplate FLA | ☐ | ☐ | ☐ |  |
| 7 | Condenser fan motor capacitor tested: within ±6% of rated MFD | ☐ | ☐ | ☐ |  |
| 8 | Outdoor unit base and mounting: level (within 1/4"), secure, and free of vegetation contact | ☐ | ☐ | ☐ |  |
| 9 | Clearances maintained: minimum 12" sides, 24" service front, unrestricted discharge top | ☐ | ☐ | ☐ |  |
| 10 | Refrigerant line set: insulation intact, supported properly, no contact with structure causing vibration | ☐ | ☐ | ☐ |  |
| 11 | Service valve caps replaced hand-tight after pressure readings | ☐ | ☐ | ☐ |  |
| 12 | Outdoor electrical disconnect: correct rating, no overheating evidence, contacts not pitted | ☐ | ☐ | ☐ |  |

⚡  SECTION 4 — ELECTRICAL COMPONENTS & CONTROLS

| # | Maintenance Task / Inspection Item | Pass | Fail | N/A | Technician Notes |
| --- | --- | --- | --- | --- | --- |
| 1 | Supply voltage measured at equipment terminals: within ±10% of nameplate rated voltage | ☐ | ☐ | ☐ |  |
| 2 | Voltage imbalance (3-phase systems): below 2% per NEMA MG-1 | ☐ | ☐ | ☐ |  |
| 3 | Compressor run capacitor tested: within ±6% of rated MFD — replace if out of range | ☐ | ☐ | ☐ |  |
| 4 | Compressor start capacitor tested (if present): within ±6% of rated MFD | ☐ | ☐ | ☐ |  |
| 5 | Condenser fan run capacitor tested: within ±6% of rated MFD | ☐ | ☐ | ☐ |  |
| 6 | Indoor blower run capacitor tested: within ±6% of rated MFD | ☐ | ☐ | ☐ |  |
| 7 | Compressor contactor: contacts inspected — not pitted, burned, or carbon-tracked; coil voltage confirmed | ☐ | ☐ | ☐ |  |
| 8 | Compressor amperage (all phases): at or below nameplate RLA at operating conditions | ☐ | ☐ | ☐ |  |
| 9 | All electrical connections tightened: torque terminals at panel, disconnect, and unit per spec | ☐ | ☐ | ☐ |  |
| 10 | Control board: no burn marks, failed LEDs, or fault codes in memory — document any stored codes | ☐ | ☐ | ☐ |  |
| 11 | Thermostat / controller: correct setpoint, time, schedule, and programming verified with customer | ☐ | ☐ | ☐ |  |
| 12 | Thermostat batteries replaced (if battery-powered or battery-backup model) | ☐ | ☐ | ☐ |  |
| 13 | Low-voltage wiring: all terminals tight, no corrosion at connections, labeling legible | ☐ | ☐ | ☐ |  |
| 14 | Crankcase heater (heat pump / low-ambient): confirmed warm — drawing rated wattage | ☐ | ☐ | ☐ |  |

Electrical Measurements

| Parameter | Design / Spec | Measured | Unit | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| Supply Voltage L1–L2 | Nameplate ±10% | ______ | ______ | ______ |  |
| Supply Voltage L1–L3 (3-phase) | Nameplate ±10% | ______ | ______ | ______ |  |
| Voltage Imbalance (3-phase %) | < 2% | ______ | ______ | ______ |  |
| Compressor Run Capacitor (MFD) | Within ±6% of rating | ______ | ______ | ______ |  |
| Condenser Fan Capacitor (MFD) | Within ±6% of rating | ______ | ______ | ______ |  |
| Indoor Blower Capacitor (MFD) | Within ±6% of rating | ______ | ______ | ______ |  |
| Compressor Amps (all phases) | At or below nameplate RLA | ______ | ______ | ______ |  |
| Condenser Fan Motor Amps | At or below nameplate FLA | ______ | ______ | ______ |  |
| Indoor Blower Motor Amps | At or below nameplate FLA | ______ | ______ | ______ |  |
| 24V Control Transformer Output | 24–28 VAC | ______ | ______ | ______ |  |

❄️  SECTION 5 — REFRIGERANT SYSTEM PERFORMANCE CHECK

| # | Maintenance Task / Inspection Item | Pass | Fail | N/A | Technician Notes |
| --- | --- | --- | --- | --- | --- |
| 1 | Refrigerant pressures taken after 10-minute stabilized runtime — not taken immediately at startup | ☐ | ☐ | ☐ |  |
| 2 | Suction pressure within expected range for refrigerant type, return air temp, and ambient | ☐ | ☐ | ☐ |  |
| 3 | Discharge pressure within expected range for refrigerant type and ambient conditions | ☐ | ☐ | ☐ |  |
| 4 | Superheat measured and within specification for system type (fixed orifice or TXV) | ☐ | ☐ | ☐ |  |
| 5 | Subcooling measured and within specification (TXV systems: 10–15°F typical) | ☐ | ☐ | ☐ |  |
| 6 | No refrigerant leak detected — electronic leak check performed at all joints, valves, coil | ☐ | ☐ | ☐ |  |
| 7 | Sight glass (if present): clear with no bubbles at stable operating conditions | ☐ | ☐ | ☐ |  |
| 8 | Suction line: cold to touch and sweating appropriately — not iced over | ☐ | ☐ | ☐ |  |
| 9 | Liquid line: warm/hot — not cold which would indicate upstream restriction | ☐ | ☐ | ☐ |  |
| 10 | System capacity confirmed: supply-to-return delta-T within spec for cooling or heating mode | ☐ | ☐ | ☐ |  |
| 11 | All refrigerant handling performed by EPA Section 608 certified technician — documented | ☐ | ☐ | ☐ |  |

Refrigerant & Performance Data

| Parameter | Design / Spec | Measured | Unit | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| Refrigerant Type | Per Nameplate | ______ | ______ | ______ |  |
| Outdoor Ambient Temp (°F) | ________ °F | ______ | ______ | ______ |  |
| Return Air Temp (°F) | ________ °F | ______ | ______ | ______ |  |
| Supply Air Temp (°F) | ________ °F | ______ | ______ | ______ |  |
| Temperature Differential ΔT (°F) | Cooling: 16–22°F / Heating: per nameplate | ______ | ______ | ______ |  |
| Suction Pressure (PSIG) | ________ PSIG | ______ | ______ | ______ |  |
| Discharge Pressure (PSIG) | ________ PSIG | ______ | ______ | ______ |  |
| Superheat (°F) | Per mfr chart | ______ | ______ | ______ |  |
| Subcooling (°F) | 10–15°F typical (TXV) | ______ | ______ | ______ |  |
| Refrigerant Added (lbs) — if any | ________ lbs | ______ | ______ | ______ |  |

🔥  SECTION 6 — GAS, COMBUSTION & HEAT EXCHANGER (HEATING SEASON)

| # | Maintenance Task / Inspection Item | Pass | Fail | N/A | Technician Notes |
| --- | --- | --- | --- | --- | --- |
| 1 | Gas supply pressure measured at appliance inlet under load — within specification | ☐ | ☐ | ☐ |  |
| 2 | Manifold gas pressure measured and verified against nameplate specification | ☐ | ☐ | ☐ |  |
| 3 | Gas valve: opens fully on W call — no chattering or delayed response | ☐ | ☐ | ☐ |  |
| 4 | All burners light evenly and fully on first ignition attempt — no delayed ignition | ☐ | ☐ | ☐ |  |
| 5 | Burner flames: stable blue with minimal yellow tipping — no lifting, rollout, or wavering | ☐ | ☐ | ☐ |  |
| 6 | Flame sensor / flame rod cleaned with emery cloth — microamp reading within spec | ☐ | ☐ | ☐ |  |
| 7 | Ignitor (HSI or spark): visually inspected for cracks; resistance measured (HSI: typically 50–200 Ω) | ☐ | ☐ | ☐ |  |
| 8 | Heat exchanger: visual inspection for rust pitting, cracks, or distortion — document findings | ☐ | ☐ | ☐ |  |
| 9 | CO test at supply register: ambient CO below 9 PPM action level — system safe to operate | ☐ | ☐ | ☐ |  |
| 10 | Flue gas analysis: CO, CO₂, O₂, and efficiency documented | ☐ | ☐ | ☐ |  |
| 11 | Induced draft motor: starts before burners, correct RPM, bearings quiet | ☐ | ☐ | ☐ |  |
| 12 | Pressure switch: closes within 3 seconds of inducer startup | ☐ | ☐ | ☐ |  |
| 13 | Limit switch: continuity confirmed at ambient temperature — has not tripped | ☐ | ☐ | ☐ |  |
| 14 | Temperature rise measured and within furnace nameplate min–max range | ☐ | ☐ | ☐ |  |
| 15 | Vent / flue connections sealed and all screws present — no gaps at joints | ☐ | ☐ | ☐ |  |

Combustion Analysis Data

| Parameter | Design / Spec | Measured | Unit | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| Gas Type | Natural Gas / LP | ______ | ______ | ______ |  |
| Supply Gas Pressure (in. w.c.) | ________ in. w.c. | ______ | ______ | ______ |  |
| Manifold Pressure (in. w.c.) | ________ in. w.c. | ______ | ______ | ______ |  |
| Flame Sensor Current (µA) | 2–8 µA typical | ______ | ______ | ______ |  |
| CO in Flue Gas (PPM undiluted) | < 400 PPM air-free | ______ | ______ | ______ |  |
| CO₂ in Flue Gas (%) | 8–10% typical | ______ | ______ | ______ |  |
| O₂ in Flue Gas (%) | 3–6% typical | ______ | ______ | ______ |  |
| Flue Gas Temperature (°F) | ________ °F | ______ | ______ | ______ |  |
| Measured Temperature Rise (°F) | ________ °F | ______ | ______ | ______ |  |
| Combustion Efficiency (%) | ________ % | ______ | ______ | ______ |  |
| Ambient CO at Supply Register (PPM) | < 9 PPM action level | ______ | ______ | ______ |  |

💨  SECTION 7 — AIRFLOW, DUCT SYSTEM & STATIC PRESSURE

| # | Maintenance Task / Inspection Item | Pass | Fail | N/A | Technician Notes |
| --- | --- | --- | --- | --- | --- |
| 1 | External static pressure measured and within equipment design specification | ☐ | ☐ | ☐ |  |
| 2 | Supply duct static pressure measured at plenum | ☐ | ☐ | ☐ |  |
| 3 | Return duct static pressure measured at return plenum | ☐ | ☐ | ☐ |  |
| 4 | All supply registers open and delivering airflow — none blocked by furniture or debris | ☐ | ☐ | ☐ |  |
| 5 | All return grilles clean and unobstructed — no furniture blocking return air pathway | ☐ | ☐ | ☐ |  |
| 6 | Duct insulation: intact in unconditioned spaces — no missing or fallen sections | ☐ | ☐ | ☐ |  |
| 7 | Duct connections at unit: sealed and secure — no air leakage audible or visible | ☐ | ☐ | ☐ |  |
| 8 | Flex duct: no kinks, excessive bends, or crushed sections limiting airflow | ☐ | ☐ | ☐ |  |
| 9 | Zone dampers (if applicable): all actuators functional — each zone opens and closes on demand | ☐ | ☐ | ☐ |  |
| 10 | Economizer (if applicable): damper opens on call and closes fully when not needed | ☐ | ☐ | ☐ |  |
| 11 | Humidity level checked and documented — dehumidification functioning if equipped | ☐ | ☐ | ☐ |  |

Airflow & Static Pressure Data

| Parameter | Design / Spec | Measured | Unit | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| External Static Pressure (in. w.c.) | Per equipment design spec | ______ | ______ | ______ |  |
| Supply Plenum Static (in. w.c.) | ________ in. w.c. | ______ | ______ | ______ |  |
| Return Plenum Static (in. w.c.) | ________ in. w.c. | ______ | ______ | ______ |  |
| Estimated Total Supply CFM | ________ CFM | ______ | ______ | ______ |  |
| Indoor Relative Humidity (%) | Target: 40–60% | ______ | ______ | ______ |  |
| Outdoor Ambient Temp (°F) | ________ °F | ______ | ______ | ______ |  |

♨️  SECTION 8 — HEAT PUMP SPECIFIC CHECKS

| # | Maintenance Task / Inspection Item | Pass | Fail | N/A | Technician Notes |
| --- | --- | --- | --- | --- | --- |
| 1 | Reversing valve: shifts correctly between heating and cooling modes — confirmed by pressure change | ☐ | ☐ | ☐ |  |
| 2 | Defrost board: initiates and terminates defrost correctly — no stuck defrost condition | ☐ | ☐ | ☐ |  |
| 3 | Outdoor coil temperature sensor: resistance within spec for current ambient temperature | ☐ | ☐ | ☐ |  |
| 4 | Defrost termination thermostat / sensor: mounted correctly on outdoor coil | ☐ | ☐ | ☐ |  |
| 5 | Crankcase heater: confirmed warm before startup in cool/cold weather | ☐ | ☐ | ☐ |  |
| 6 | Low-ambient lockout setting verified: compressor does not operate below rated minimum | ☐ | ☐ | ☐ |  |
| 7 | Auxiliary / emergency heat staging: energizes on high demand and emergency heat mode | ☐ | ☐ | ☐ |  |
| 8 | Balance point and auxiliary heat setpoint confirmed correct for local climate | ☐ | ☐ | ☐ |  |
| 9 | HSPF2 / COP performance consistent with ambient conditions and measured data | ☐ | ☐ | ☐ |  |

📊  SECTION 9 — COMPONENT CONDITION RATINGS & REMAINING LIFE ESTIMATE

| Component / Item | Condition Rating | Recommended Action |
| --- | --- | --- |
| Compressor (outdoor unit) | ☐ Good ☐ Fair ☐ Poor |  |
| Condenser Fan Motor | ☐ Good ☐ Fair ☐ Poor |  |
| Condenser Coil Condition | ☐ Good ☐ Fair ☐ Poor |  |
| Indoor Blower Motor | ☐ Good ☐ Fair ☐ Poor |  |
| Evaporator Coil Condition | ☐ Good ☐ Fair ☐ Poor |  |
| Run Capacitor(s) | ☐ Good ☐ Fair ☐ Poor |  |
| Contactor | ☐ Good ☐ Fair ☐ Poor |  |
| Control Board | ☐ Good ☐ Fair ☐ Poor |  |
| Heat Exchanger (gas systems) | ☐ Good ☐ Fair ☐ Poor |  |
| Burner Assembly (gas systems) | ☐ Good ☐ Fair ☐ Poor |  |
| Flue / Vent System (gas systems) | ☐ Good ☐ Fair ☐ Poor |  |
| Refrigerant Charge Level | ☐ Good ☐ Fair ☐ Poor |  |
| Duct System Condition | ☐ Good ☐ Fair ☐ Poor |  |
| Thermostat / Controls | ☐ Good ☐ Fair ☐ Poor |  |
| Electrical Wiring & Connections | ☐ Good ☐ Fair ☐ Poor |  |
| Drain System (pan, line, pump) | ☐ Good ☐ Fair ☐ Poor |  |
| Filter / Air Quality Equipment | ☐ Good ☐ Fair ☐ Poor |  |
| Overall System Condition | ☐ Good ☐ Fair ☐ Poor |  |

Estimated Remaining Useful Life:  ________ years          Replacement Recommended Within:  ☐ 1 yr    ☐ 2–3 yrs    ☐ 5+ yrs    ☐ N/A

📋  SECTION 10 — RECOMMENDATIONS, REPAIRS NEEDED & CUSTOMER ADVISORY

| # | Recommended Repair / Item | Priority | Est. Cost | Customer Decision |
| --- | --- | --- | --- | --- |
| 1 |  | ☐ Urgent ☐ Soon ☐ Advisory | $________ | ☐ Approved ☐ Declined ☐ Pending |
| 2 |  | ☐ Urgent ☐ Soon ☐ Advisory | $________ | ☐ Approved ☐ Declined ☐ Pending |
| 3 |  | ☐ Urgent ☐ Soon ☐ Advisory | $________ | ☐ Approved ☐ Declined ☐ Pending |
| 4 |  | ☐ Urgent ☐ Soon ☐ Advisory | $________ | ☐ Approved ☐ Declined ☐ Pending |
| 5 |  | ☐ Urgent ☐ Soon ☐ Advisory | $________ | ☐ Approved ☐ Declined ☐ Pending |
| 6 |  | ☐ Urgent ☐ Soon ☐ Advisory | $________ | ☐ Approved ☐ Declined ☐ Pending |
| 7 |  | ☐ Urgent ☐ Soon ☐ Advisory | $________ | ☐ Approved ☐ Declined ☐ Pending |

| TUNE-UP COMPLETION SUMMARY |  |  |  |
| --- | --- | --- | --- |
| Total Items Inspected: | ________ | Items Passing: | ________ |
| Items Requiring Attention: | ________ | Items N/A: | ________ |
| Tune-Up Result: | ☐ Complete ☐ Complete w/ Deficiencies ☐ Incomplete | Follow-Up Required: | ☐ Yes ☐ No |
| Refrigerant Added (lbs): | ________ | Refrigerant Type: | ________ |
| Filter Replaced: | ☐ Yes ☐ No ☐ Customer Supplied | Next Service Due: | ____________ |
| Service Agreement Renewed: | ☐ Yes ☐ No ☐ Offered | Total Service Time (hrs): | ________ |

✅  SECTION 11 — TECHNICIAN SIGN-OFF & CUSTOMER ACCEPTANCE

| TECHNICIAN SIGN-OFF & CUSTOMER ACCEPTANCE |  |
| --- | --- |
| HVAC Technician Name: ________________________________ Signature: ___________________________ Company: ____________________________ Date / Time: ________________________ | Customer / Authorized Representative Name: ________________________________ Signature: ___________________________ Company: ____________________________ Date / Time: ________________________ |

TECHNICIAN CERTIFICATION & CUSTOMER SATISFACTION By signing above, the HVAC Technician certifies that all maintenance tasks and inspections recorded on this form were performed during this service visit, that all measurements were taken with calibrated instruments, and that any safety hazards discovered were communicated to the customer. All refrigerant handling was performed by an EPA Section 608 certified technician per 40 CFR Part 82. Customer signature confirms satisfactory completion of the tune-up service and acknowledgment of all recommendations and advisories communicated during this visit. Customer Satisfaction Rating: ☐ Excellent ☐ Good ☐ Satisfactory ☐ Needs Follow-Up