HVAC SYSTEM ASSESSMENT CHECKLIST Complete all applicable sections. Mark Pass / Fail / N/A. Record all measurements and observations.

📋  SECTION 1 — JOB & TECHNICIAN INFORMATION

| Work Order #: ________________________ | Assessment Date: ________________________ |
| --- | --- |
| Technician Name: ________________________ | Certification / License #: ________________________ |
| Supervisor / Lead Tech: ________________________ | Assessment Type: ________________________ |

| Client / Company Name: ________________________ | Site Contact Name: ________________________ |
| --- | --- |
| Site Address: ________________________ | Phone / Email: ________________________ |
| Building Name / Suite: ________________________ | Floor / Zone: ________________________ |

🏷️  SECTION 2 — SYSTEM IDENTIFICATION

| Equipment Type: ________________________ | System Tag / Unit ID: ________________________ |
| --- | --- |
| Manufacturer: ________________________ | Model Number: ________________________ |
| Serial Number: ________________________ | Year Manufactured: ________________________ |
| Refrigerant Type: ________________________ | Refrigerant Circuit Charge (lbs): ________________________ |
| Voltage / Phase / Hz: ________________________ | Amperage (MCA / MOP): ________________________ |
| Last Service Date: ________________________ | Previous Technician: ________________________ |

Assessment Scope

Assessment Purpose: ☐ Pre-Season ☐ Post-Repair ☐ New Install ☐ Annual PM ☐ Complaint-Driven Ambient Temp (°F): Relative Humidity (%): Special Conditions / Notes:

⚠️  SECTION 3 — SAFETY & LOCKOUT / TAGOUT VERIFICATION

| Item / Inspection Point | Pass | Fail | N/A | Notes / Observations |
| --- | --- | --- | --- | --- |
| LOTO procedures reviewed and followed per OSHA 29 CFR 1910.147 | ☐ | ☐ | ☐ |  |
| All power sources identified and de-energized prior to work | ☐ | ☐ | ☐ |  |
| Lockout devices applied and tags attached | ☐ | ☐ | ☐ |  |
| PPE worn — safety glasses, gloves, arc flash protection as required | ☐ | ☐ | ☐ |  |
| Area clear of obstructions; work zone secured | ☐ | ☐ | ☐ |  |
| Refrigerant recovery equipment available and in calibration | ☐ | ☐ | ☐ |  |
| Manifold gauges / digital gauges calibrated within 12 months | ☐ | ☐ | ☐ |  |
| Emergency shut-off location confirmed with site contact | ☐ | ☐ | ☐ |  |
| Gas leak detector functional and on-site | ☐ | ☐ | ☐ |  |
| Combustible gas / CO detector available (gas-fired systems) | ☐ | ☐ | ☐ |  |

⚡  SECTION 4 — ELECTRICAL ASSESSMENT

4A — Visual & Physical Electrical Inspection

| Item / Inspection Point | Pass | Fail | N/A | Notes / Observations |
| --- | --- | --- | --- | --- |
| Disconnect switch / breaker labeled and accessible | ☐ | ☐ | ☐ |  |
| Electrical panel / control box free of corrosion and pest infiltration | ☐ | ☐ | ☐ |  |
| All wiring connections tight — no loose, burnt, or chafed conductors | ☐ | ☐ | ☐ |  |
| Capacitors (run & start) visually inspected — no bulging or leakage | ☐ | ☐ | ☐ |  |
| Contactors inspected — contacts not pitted, pocked, or arced | ☐ | ☐ | ☐ |  |
| Relays and control boards — no signs of overheating or burn marks | ☐ | ☐ | ☐ |  |
| Ground wires present and connected at all terminals | ☐ | ☐ | ☐ |  |
| Low-voltage control wiring routed and protected properly | ☐ | ☐ | ☐ |  |
| High-voltage wiring secured with appropriate fittings | ☐ | ☐ | ☐ |  |
| Crankcase heater operational (compressor systems) | ☐ | ☐ | ☐ |  |

4B — Electrical Measurements

| Parameter | Measured | Unit | Specification | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| Supply Voltage — L1 to L2 |  | VAC | Nameplate ±10% |  |  |
| Supply Voltage — L1 to L3 |  | VAC | Nameplate ±10% |  |  |
| Supply Voltage — L2 to L3 |  | VAC | Nameplate ±10% |  |  |
| Compressor RLA / FLA |  | Amps | Nameplate RLA |  |  |
| Compressor Start Amps (LRA) |  | Amps | Nameplate LRA |  |  |
| Condenser Fan Motor Amps |  | Amps | Nameplate FLA |  |  |
| Blower Motor Amps |  | Amps | Nameplate FLA |  |  |
| Run Capacitor — Compressor |  | µF | Rating ±6% |  |  |
| Run Capacitor — Fan Motor |  | µF | Rating ±6% |  |  |
| Start Capacitor (if equipped) |  | µF | Rating ±20% |  |  |
| Contactor Voltage Drop |  | VDC | < 0.2 VDC |  |  |

🌡️  SECTION 5 — REFRIGERATION CIRCUIT ASSESSMENT

5A — Refrigeration System Visual Inspection

| Item / Inspection Point | Pass | Fail | N/A | Notes / Observations |
| --- | --- | --- | --- | --- |
| Refrigerant circuit leak-checked — all joints, fittings, and coil connections | ☐ | ☐ | ☐ |  |
| No oil staining on refrigerant lines, coils, or fittings | ☐ | ☐ | ☐ |  |
| Refrigerant lines properly insulated and secured | ☐ | ☐ | ☐ |  |
| Sight glass clear — no bubbles (liquid line, full charge) | ☐ | ☐ | ☐ |  |
| Filter-drier condition checked — no excessive pressure drop | ☐ | ☐ | ☐ |  |
| TXV / EXV operation verified (if equipped) | ☐ | ☐ | ☐ |  |
| Metering device adjusted or noted for future service | ☐ | ☐ | ☐ |  |
| Reversing valve operation confirmed (heat pump systems) | ☐ | ☐ | ☐ |  |
| Accumulator inspected for oil trapping (suction line) | ☐ | ☐ | ☐ |  |
| Hot gas bypass valve set point verified (if equipped) | ☐ | ☐ | ☐ |  |

5B — Refrigeration System Measurements

| Parameter | Measured | Unit | Specification | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| Suction Pressure |  | PSIG | Per mfr. chart |  |  |
| Discharge Pressure |  | PSIG | Per mfr. chart |  |  |
| Suction Saturation Temp (SST) |  | °F | Per conditions |  |  |
| Discharge Saturation Temp (DST) |  | °F | Per conditions |  |  |
| Suction Line Temp (at service valve) |  | °F | SST + superheat |  |  |
| Superheat (Suction) |  | °F | 5–20°F target |  |  |
| Liquid Line Temp (at liquid valve) |  | °F | DST - subcool |  |  |
| Subcooling (Liquid) |  | °F | 10–20°F target |  |  |
| Compressor Discharge Temp |  | °F | < 225°F |  |  |
| Refrigerant Added / Removed |  | lbs | — |  |  |

💨  SECTION 6 — AIRSIDE & MECHANICAL ASSESSMENT

6A — Air Handler / Blower Unit

| Item / Inspection Point | Pass | Fail | N/A | Notes / Observations |
| --- | --- | --- | --- | --- |
| Blower wheel clean — no buildup or debris | ☐ | ☐ | ☐ |  |
| Blower motor bearings lubricated (sleeve-bearing motors) | ☐ | ☐ | ☐ |  |
| Belt drive checked — tension, alignment, and wear (if equipped) | ☐ | ☐ | ☐ |  |
| Direct-drive motor coupling inspected (if equipped) | ☐ | ☐ | ☐ |  |
| Blower housing free of cracks, corrosion, or gaps | ☐ | ☐ | ☐ |  |
| Evaporator coil clean — no blockage or biological growth | ☐ | ☐ | ☐ |  |
| Evaporator coil fins straight — combed if necessary | ☐ | ☐ | ☐ |  |
| Secondary / primary drain pan clean and slope verified | ☐ | ☐ | ☐ |  |
| Condensate drain line flushed and flowing freely | ☐ | ☐ | ☐ |  |
| Condensate trap depth adequate for system static | ☐ | ☐ | ☐ |  |
| Air filter replaced or cleaned — MERV rating documented | ☐ | ☐ | ☐ |  |
| Filter rack / housing sealing properly — no bypass | ☐ | ☐ | ☐ |  |
| Supply plenum insulation intact — no gaps or tears | ☐ | ☐ | ☐ |  |

6B — Condenser / Outdoor Unit

| Item / Inspection Point | Pass | Fail | N/A | Notes / Observations |
| --- | --- | --- | --- | --- |
| Condenser coil cleaned — fins inspected and straightened | ☐ | ☐ | ☐ |  |
| Condenser fan blade pitch correct — no cracks or imbalance | ☐ | ☐ | ☐ |  |
| Condenser fan guard / grille in place and secure | ☐ | ☐ | ☐ |  |
| Unit pad / curb level — no settling or tipping | ☐ | ☐ | ☐ |  |
| Clearance maintained — 12" minimum all sides, 24" service side | ☐ | ☐ | ☐ |  |
| Refrigerant line insulation intact at condenser connections | ☐ | ☐ | ☐ |  |
| Rain/debris shield in place (if required) | ☐ | ☐ | ☐ |  |
| Unit electrical cover panels secured | ☐ | ☐ | ☐ |  |

6C — Airflow Measurements

| Parameter | Measured | Unit | Specification | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| Total External Static Pressure (TESP) |  | in. w.c. | Mfr. spec |  |  |
| Entering Wet-Bulb Temperature |  | °F | — |  |  |
| Leaving Wet-Bulb Temperature |  | °F | — |  |  |
| Entering Dry-Bulb Temperature |  | °F | — |  |  |
| Leaving Dry-Bulb Temperature |  | °F | — |  |  |
| Temperature Split (ΔT) |  | °F | 16–22°F cooling |  |  |
| Total CFM (measured / design) |  | CFM | Design CFM |  |  |
| Blower Motor RPM |  | RPM | Nameplate |  |  |
| Heating Rise (gas / electric) |  | °F | Per mfr. spec |  |  |

🎛️  SECTION 7 — CONTROLS & THERMOSTAT ASSESSMENT

| Item / Inspection Point | Pass | Fail | N/A | Notes / Observations |
| --- | --- | --- | --- | --- |
| Thermostat / DDC controller firmware up to date | ☐ | ☐ | ☐ |  |
| Thermostat set points verified — cooling, heating, fan mode | ☐ | ☐ | ☐ |  |
| Thermostat location and mounting — away from heat sources | ☐ | ☐ | ☐ |  |
| Temperature calibration checked (stat vs. calibrated thermometer) | ☐ | ☐ | ☐ |  |
| Economizer / free-cooling operation verified (if equipped) | ☐ | ☐ | ☐ |  |
| Demand-controlled ventilation (DCV) CO₂ sensor calibrated | ☐ | ☐ | ☐ |  |
| BAS / BMS integration points confirmed (if applicable) | ☐ | ☐ | ☐ |  |
| Scheduling / occupied-unoccupied modes programmed and active | ☐ | ☐ | ☐ |  |
| Low-ambient lockout controls set per mfr. specifications | ☐ | ☐ | ☐ |  |
| High-pressure / low-pressure controls tested (manual reset) | ☐ | ☐ | ☐ |  |
| Freeze-stat setpoint and operation verified (AHU coil protection) | ☐ | ☐ | ☐ |  |
| Time delays (anti-short cycle, fan off-delay) functional | ☐ | ☐ | ☐ |  |
| Emergency heat or backup heat staging verified (heat pump) | ☐ | ☐ | ☐ |  |

🔥  SECTION 8 — GAS & COMBUSTION ASSESSMENT (Gas Systems Only)

8A — Gas System Visual Inspection

| Item / Inspection Point | Pass | Fail | N/A | Notes / Observations |
| --- | --- | --- | --- | --- |
| Gas supply shut-off valve accessible and labeled | ☐ | ☐ | ☐ |  |
| Gas line free of leaks — checked with detector or soap solution | ☐ | ☐ | ☐ |  |
| Gas pressure verified at unit — matches nameplate spec | ☐ | ☐ | ☐ |  |
| Burners clean — no carbon buildup, rust, or scaling | ☐ | ☐ | ☐ |  |
| Heat exchanger inspected — no cracks, holes, or stress fractures | ☐ | ☐ | ☐ |  |
| Igniter / spark electrode clean and properly gapped | ☐ | ☐ | ☐ |  |
| Flame sensor / rod clean and securely mounted | ☐ | ☐ | ☐ |  |
| Induced draft / combustion blower wheel clean and spinning freely | ☐ | ☐ | ☐ |  |
| Flue / vent pipe secure, sloped correctly, and free of blockage | ☐ | ☐ | ☐ |  |
| Combustion air pathway clear and unobstructed | ☐ | ☐ | ☐ |  |
| Pressure switch(es) operation verified | ☐ | ☐ | ☐ |  |
| Roll-out switch condition and operation verified | ☐ | ☐ | ☐ |  |

8B — Combustion Measurements

| Parameter | Measured | Unit | Specification | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| Gas Supply Pressure (in. w.c.) |  | in. w.c. | Mfr. spec |  |  |
| Gas Manifold Pressure (in. w.c.) |  | in. w.c. | Mfr. spec |  |  |
| CO (Carbon Monoxide) — Flue Gas |  | ppm | < 400 ppm undiluted |  |  |
| CO₂ — Flue Gas |  | % | 7–10% natural gas |  |  |
| O₂ — Flue Gas |  | % | 3–6% |  |  |
| Flue Gas Temperature |  | °F | Per mfr. spec |  |  |
| Combustion Efficiency |  | % | > 80% |  |  |
| Ambient CO — Equipment Room |  | ppm | < 9 ppm (OSHA) |  |  |

🌬️  SECTION 9 — IAQ & VENTILATION ASSESSMENT

| Item / Inspection Point | Pass | Fail | N/A | Notes / Observations |
| --- | --- | --- | --- | --- |
| Outside air damper operation and position verified | ☐ | ☐ | ☐ |  |
| Minimum OA CFM verified per ASHRAE 62.1 requirements | ☐ | ☐ | ☐ |  |
| Return air path clear — no blockage or pressure imbalance | ☐ | ☐ | ☐ |  |
| Supply grilles / diffusers free of debris, mold, or corrosion | ☐ | ☐ | ☐ |  |
| Duct system — no visible leakage, disconnections, or damage | ☐ | ☐ | ☐ |  |
| Ultraviolet (UV) germicidal lamps operational — hours logged | ☐ | ☐ | ☐ |  |
| Electronic air cleaner cells cleaned and reinstalled | ☐ | ☐ | ☐ |  |
| HEPA / high-efficiency filtration condition checked | ☐ | ☐ | ☐ |  |
| Drain pans free of standing water, mold, and biological growth | ☐ | ☐ | ☐ |  |
| Humidifier / dehumidifier operation and set points verified | ☐ | ☐ | ☐ |  |
| Exhaust fans operational and balanced with supply | ☐ | ☐ | ☐ |  |

IAQ Spot Measurements

| Parameter | Measured | Unit | Specification | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| Supply Air CO₂ (ppm) |  | ppm | < 1100 ppm |  |  |
| Return Air CO₂ (ppm) |  | ppm | < 1100 ppm |  |  |
| Space CO₂ — Zone 1 |  | ppm | < 1100 ppm |  |  |
| Space RH — Zone 1 |  | % | 30–60% |  |  |
| Space Temp — Zone 1 |  | °F | Set point ±2°F |  |  |
| TVOC (if measured) |  | µg/m³ | < 500 µg/m³ |  |  |
| Particulate PM2.5 (if measured) |  | µg/m³ | < 12 µg/m³ (24hr) |  |  |

📊  SECTION 10 — FINDINGS SUMMARY & RECOMMENDATIONS

Overall Assessment Result: ☐ PASS — System operating within acceptable parameters ☐ FAIL — Deficiencies found, follow-up required ☐ CONDITIONAL — See notes

Immediate Action Items (Safety-Critical): 1. _______________________________________________________________________________ 2. _______________________________________________________________________________ 3. _______________________________________________________________________________

Recommended Repairs / Future Service Items: 1. _______________________________________________________________________________ 2. _______________________________________________________________________________ 3. _______________________________________________________________________________ 4. _______________________________________________________________________________

✍️  SECTION 11 — AUTHORIZATION & SIGNATURES

| Technician Name (Print) | Technician Signature | Date |
| --- | --- | --- |

| Supervisor / Lead Technician | Supervisor Signature | Date |
| --- | --- | --- |

| Customer / Site Representative (Print) | Customer Signature | Date Accepted |
| --- | --- | --- |

Customer Authorization: I authorize work described above and confirm system assessment has been reviewed with me.