HVAC SYSTEM ENERGY & COMPLIANCE AUDIT CHECKLIST Complete all applicable sections. Score each category. Document all findings and priority recommendations.

📋  SECTION 1 — AUDIT SCOPE & FACILITY INFORMATION

| Audit Report #: ________________________ | Audit Date: ________________________ |
| --- | --- |
| Lead Auditor: ________________________ | Auditor Certification / License #: ________________________ |
| Co-Auditor / Witness: ________________________ | Auditing Firm / Company: ________________________ |

| Facility / Client Name: ________________________ | Primary Contact Name: ________________________ |
| --- | --- |
| Facility Address: ________________________ | Phone / Email: ________________________ |
| Building Type: ________________________ | Year Constructed: ________________________ |
| Total Conditioned Area (sq ft): ________________________ | Number of Floors / Zones: ________________________ |
| Hours of Operation: ________________________ | Occupancy Type: ________________________ |

Audit Scope & Objectives

Audit Type: ☐ Energy Audit ☐ Compliance Audit ☐ Preventive Maintenance Audit ☐ Full Facility HVAC Audit Audit Trigger: ☐ Owner Request ☐ Utility Incentive ☐ Code Enforcement ☐ Insurance ☐ Lease Requirement Standards Referenced: ☐ ASHRAE 62.1 ☐ ASHRAE 90.1 ☐ IMC ☐ IECC ☐ Local Code ☐ EPA 608 Previous Audit Date: Last Audit Score: ____________ Utility Account(s): Electric: _________________________ Gas: _________________________

🏷️  SECTION 2 — HVAC EQUIPMENT INVENTORY

Equipment Inventory Summary — Complete one row per major HVAC unit

| Unit ID | Equipment Type | Manufacturer / Model | Serial # | Tons/MBH | Year | Condition |
| --- | --- | --- | --- | --- | --- | --- |
| AHU-01 |  |  |  |  |  | ☐ Good ☐ Fair ☐ Poor |
| AHU-02 |  |  |  |  |  | ☐ Good ☐ Fair ☐ Poor |
| AHU-03 |  |  |  |  |  | ☐ Good ☐ Fair ☐ Poor |
| AHU-04 |  |  |  |  |  | ☐ Good ☐ Fair ☐ Poor |
| AHU-05 |  |  |  |  |  | ☐ Good ☐ Fair ☐ Poor |
| AHU-06 |  |  |  |  |  | ☐ Good ☐ Fair ☐ Poor |
| AHU-07 |  |  |  |  |  | ☐ Good ☐ Fair ☐ Poor |
| AHU-08 |  |  |  |  |  | ☐ Good ☐ Fair ☐ Poor |

⚡  SECTION 3 — ENERGY PERFORMANCE AUDIT

3A — Energy Consumption Baseline

12-Month Electric Use (kWh): __________________ Avg Monthly: __________________ 12-Month Gas Use (therms / CCF): __________________ Avg Monthly: __________________ Annual Energy Cost: Electric: $______________ Gas: $______________ Total: $______________ Energy Use Intensity (EUI): __________________ kBtu/sq ft/yr Benchmark EUI: __________________ Utility Rate — Electric: $____________/kWh Demand Charge: $____________/kW Utility Rate — Gas: $____________/therm

3B — Energy Efficiency Audit Checklist

| Item / Audit Point | Pass | Fail | N/A | Notes / Findings |
| --- | --- | --- | --- | --- |
| Building energy model or energy analysis available and reviewed | ☐ | ☐ | ☐ |  |
| HVAC accounts for documented % of total building energy (target < 40% commercial) | ☐ | ☐ | ☐ |  |
| Equipment EER / SEER / COP meets or exceeds ASHRAE 90.1 minimum efficiency | ☐ | ☐ | ☐ |  |
| Variable frequency drives (VFDs) installed on all motors > 5 HP | ☐ | ☐ | ☐ |  |
| Economizer / free-cooling operation functional and controls verified | ☐ | ☐ | ☐ |  |
| Demand-controlled ventilation (DCV) with CO₂ sensors operational | ☐ | ☐ | ☐ |  |
| Night setback / scheduling programmed and confirmed active | ☐ | ☐ | ☐ |  |
| Occupancy sensors integrated with HVAC controls | ☐ | ☐ | ☐ |  |
| Energy recovery ventilation (ERV/HRV) operational (if equipped) | ☐ | ☐ | ☐ |  |
| Heating and cooling not operating simultaneously — deadband verified | ☐ | ☐ | ☐ |  |
| Simultaneous heating and cooling identified in any zone | ☐ | ☐ | ☐ |  |
| Supply air temperature reset strategy implemented | ☐ | ☐ | ☐ |  |
| Duct system leakage tested — leakage < 4% total airflow | ☐ | ☐ | ☐ |  |
| Pipe insulation intact on all hot and chilled water distribution lines | ☐ | ☐ | ☐ |  |
| Refrigerant charge verified correct — no over/undercharge condition | ☐ | ☐ | ☐ |  |

3C — Energy Performance Measurements

| Parameter | Measured | Unit | Specification | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| System EER (cooling) |  | BTU/W·hr | ≥ ASHRAE 90.1 min |  |  |
| System COP (heating) |  | — | ≥ ASHRAE 90.1 min |  |  |
| Actual kW Demand — Peak |  | kW | Per baseline |  |  |
| Avg Supply Air Temp — Cooling |  | °F | Per design |  |  |
| Avg Supply Air Temp — Heating |  | °F | Per design |  |  |
| Chilled Water Supply Temp (CHW) |  | °F | 44–46°F typical |  |  |
| Hot Water Supply Temp (HHW) |  | °F | Per design |  |  |
| Economizer Enthalpy Set Point |  | BTU/lb | Per local climate |  |  |
| Fan BHP (measured vs. design) |  | HP | Design BHP |  |  |
| Estimated Annual HVAC Energy |  | kBtu | Baseline |  |  |

⚙️  SECTION 4 — MECHANICAL SYSTEMS AUDIT

4A — Air Distribution & Ductwork

| Item / Audit Point | Pass | Fail | N/A | Notes / Findings |
| --- | --- | --- | --- | --- |
| Duct system designed per ACCA Manual D or equivalent standard | ☐ | ☐ | ☐ |  |
| Supply duct insulation R-value meets code (R-6 unconditioned / R-4 conditioned space) | ☐ | ☐ | ☐ |  |
| Return duct insulation in place and intact | ☐ | ☐ | ☐ |  |
| Duct connections sealed with mastic or UL-181 tape — no foil tape only | ☐ | ☐ | ☐ |  |
| Flexible duct fully extended — no kinks, sags, or compressions | ☐ | ☐ | ☐ |  |
| Supply and return grilles/diffusers clean, undamaged, and properly positioned | ☐ | ☐ | ☐ |  |
| No duct disconnections, holes, or uncapped branch takeoffs found | ☐ | ☐ | ☐ |  |
| Balancing dampers accessible, labeled, and positions documented | ☐ | ☐ | ☐ |  |
| VAV boxes functional — actuators operational, dampers not stuck open or closed | ☐ | ☐ | ☐ |  |
| Terminal unit filters (fan-powered VAVs) clean and in place | ☐ | ☐ | ☐ |  |
| Duct acoustical liner intact — no deterioration or exposed fibers | ☐ | ☐ | ☐ |  |
| Smoke and fire dampers accessible and tested per NFPA 105 | ☐ | ☐ | ☐ |  |

4B — Piping Systems (Hydronic & Refrigerant)

| Item / Audit Point | Pass | Fail | N/A | Notes / Findings |
| --- | --- | --- | --- | --- |
| Chilled water / hot water piping insulation intact — no wet, missing, or damaged sections | ☐ | ☐ | ☐ |  |
| Piping system free of visible leaks, staining, or corrosion | ☐ | ☐ | ☐ |  |
| Expansion tanks properly charged and functional | ☐ | ☐ | ☐ |  |
| Pumps operating — no excess vibration, bearing noise, or seal leakage | ☐ | ☐ | ☐ |  |
| Strainers clean — pressure drop within normal range | ☐ | ☐ | ☐ |  |
| Chemical water treatment program in place and analysis current | ☐ | ☐ | ☐ |  |
| Refrigerant line insulation intact — vapor barrier sealed at all joints | ☐ | ☐ | ☐ |  |
| Condensate piping pitched correctly and draining freely | ☐ | ☐ | ☐ |  |
| Hydronic system balanced — flow rates documented per design | ☐ | ☐ | ☐ |  |
| Pressure differential across coils within design range | ☐ | ☐ | ☐ |  |

4C — Hydronic System Measurements

| Parameter | Measured | Unit | Specification | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| Chilled Water Supply Temp |  | °F | 44–46°F |  |  |
| Chilled Water Return Temp |  | °F | 54–56°F |  |  |
| Chilled Water Delta-T |  | °F | 8–12°F target |  |  |
| Hot Water Supply Temp |  | °F | Per design |  |  |
| Hot Water Return Temp |  | °F | Per design |  |  |
| System Static Pressure |  | PSIG | Per design |  |  |
| Differential Pressure (pump) |  | ft H₂O | Per design |  |  |
| Condenser Water Supply (cooling tower) |  | °F | 85°F typical |  |  |
| Condenser Water Return (cooling tower) |  | °F | 95°F typical |  |  |
| Water Treatment pH |  | pH | 7.0–8.5 |  |  |

🎛️  SECTION 5 — CONTROLS & BUILDING AUTOMATION SYSTEM (BAS) AUDIT

| Item / Audit Point | Pass | Fail | N/A | Notes / Findings |
| --- | --- | --- | --- | --- |
| BAS / BMS system operational — no persistent alarms or faults | ☐ | ☐ | ☐ |  |
| All control sequences documented and verified against sequences of operation | ☐ | ☐ | ☐ |  |
| Temperature sensors calibrated — variance < 1°F from reference thermometer | ☐ | ☐ | ☐ |  |
| Humidity sensors calibrated — variance < 3% RH from reference | ☐ | ☐ | ☐ |  |
| CO₂ sensors calibrated — variance < 50 ppm from reference standard | ☐ | ☐ | ☐ |  |
| Pressure sensors and differential pressure transmitters calibrated | ☐ | ☐ | ☐ |  |
| Control valves operational — no hunting, sticking, or full-open/closed failure | ☐ | ☐ | ☐ |  |
| Damper actuators operational — full travel verified on all units | ☐ | ☐ | ☐ |  |
| System trends / data logging enabled and data being recorded | ☐ | ☐ | ☐ |  |
| Fault detection and diagnostics (FDD) rules active (if equipped) | ☐ | ☐ | ☐ |  |
| All active BAS alarms reviewed, documented, and ownership assigned | ☐ | ☐ | ☐ |  |
| Remote access and cybersecurity controls documented and in place | ☐ | ☐ | ☐ |  |
| Control panel enclosures clean, dry, and secured | ☐ | ☐ | ☐ |  |
| Software / firmware current — patches applied | ☐ | ☐ | ☐ |  |
| Sequences of operation available and current (as-built revisions) | ☐ | ☐ | ☐ |  |

🌬️  SECTION 6 — IAQ & VENTILATION COMPLIANCE AUDIT

6A — Ventilation Code Compliance (ASHRAE 62.1)

| Item / Audit Point | Pass | Fail | N/A | Notes / Findings |
| --- | --- | --- | --- | --- |
| Minimum OA CFM calculated per ASHRAE 62.1 Ventilation Rate Procedure | ☐ | ☐ | ☐ |  |
| Outdoor air intakes free of blockage, debris, bird nests, and obstructions | ☐ | ☐ | ☐ |  |
| OA intake minimum separation distance from exhaust, loading docks, and parking maintained | ☐ | ☐ | ☐ |  |
| Outside air dampers open to minimum position during all occupied hours | ☐ | ☐ | ☐ |  |
| Relief / exhaust air paths unobstructed — no recirculation of exhaust into OA intake | ☐ | ☐ | ☐ |  |
| All exhaust fans operational — toilet rooms, kitchens, janitor closets | ☐ | ☐ | ☐ |  |
| Make-up air units providing required CFM where required by code | ☐ | ☐ | ☐ |  |
| Pressurization relationships between spaces correct (positive / negative as designed) | ☐ | ☐ | ☐ |  |
| Filtration meets ASHRAE 62.1 minimum — MERV rating confirmed | ☐ | ☐ | ☐ |  |
| Air balancing report available and current (within 2 years) | ☐ | ☐ | ☐ |  |

6B — IAQ Field Measurements

| Parameter | Measured | Unit | Specification | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| OA CFM — AHU-01 (measured vs. design) |  | CFM | Design OA CFM |  |  |
| OA CFM — AHU-02 (measured vs. design) |  | CFM | Design OA CFM |  |  |
| Space CO₂ — Zone 1 (worst case) |  | ppm | < 1100 ppm |  |  |
| Space CO₂ — Zone 2 |  | ppm | < 1100 ppm |  |  |
| Space RH — Zone 1 |  | % | 30–60% RH |  |  |
| Space Temp — Zone 1 |  | °F | Set point ±2°F |  |  |
| TVOC (representative zone) |  | µg/m³ | < 500 µg/m³ |  |  |
| PM2.5 (representative zone) |  | µg/m³ | < 12 µg/m³ |  |  |
| Formaldehyde (if tested) |  | ppb | < 27 ppb (OSHA) |  |  |

🌡️  SECTION 7 — REFRIGERANT COMPLIANCE & LEAK DETECTION

| Item / Audit Point | Pass | Fail | N/A | Notes / Findings |
| --- | --- | --- | --- | --- |
| All refrigerant types identified and documented — no non-compliant blends | ☐ | ☐ | ☐ |  |
| HFO / low-GWP refrigerant transition plan in place (EPA AIM Act compliance) | ☐ | ☐ | ☐ |  |
| EPA Section 608 certified technician performed all refrigerant work | ☐ | ☐ | ☐ |  |
| Refrigerant purchase and recovery records maintained and available | ☐ | ☐ | ☐ |  |
| Appliance leak rate verified — annual leak rate does not exceed EPA threshold (10%) | ☐ | ☐ | ☐ |  |
| Refrigerant tracking log current — charges, recoveries, and additions documented | ☐ | ☐ | ☐ |  |
| Recovery cylinders labeled, inspected, and within hydrostatic test date | ☐ | ☐ | ☐ |  |
| Manifold gauges and recovery equipment calibrated within 12 months | ☐ | ☐ | ☐ |  |
| Full refrigerant leak detection survey completed — no active leaks found | ☐ | ☐ | ☐ |  |
| Refrigerant logs available and organized for regulatory inspection | ☐ | ☐ | ☐ |  |

🔧  SECTION 8 — PREVENTIVE MAINTENANCE PROGRAM AUDIT

| Item / Audit Point | Pass | Fail | N/A | Notes / Findings |
| --- | --- | --- | --- | --- |
| PM program in place — written schedule or CMMS work orders documented | ☐ | ☐ | ☐ |  |
| Filter change frequency appropriate for application and filter MERV rating | ☐ | ☐ | ☐ |  |
| Coil cleaning frequency documented and all coils currently clean | ☐ | ☐ | ☐ |  |
| Belt drives inspected and replaced on schedule — tension and alignment documented | ☐ | ☐ | ☐ |  |
| Lubrication schedule followed — oil type and quantity documented per unit | ☐ | ☐ | ☐ |  |
| Condensate system flushed per schedule — no biological growth present | ☐ | ☐ | ☐ |  |
| UV germicidal lamp hours tracked — replacement schedule followed | ☐ | ☐ | ☐ |  |
| Heat exchanger inspected annually (all gas-fired systems) | ☐ | ☐ | ☐ |  |
| Ignition system components replaced per manufacturer schedule | ☐ | ☐ | ☐ |  |
| Refrigerant circuit leak-checked at each PM visit — log current | ☐ | ☐ | ☐ |  |
| Electrical connections tightened per torque specifications at annual PM | ☐ | ☐ | ☐ |  |
| Control calibration performed at least annually | ☐ | ☐ | ☐ |  |
| Equipment run hours logged — deferred maintenance items tracked in CMMS | ☐ | ☐ | ☐ |  |
| PM completion rate > 90% over past 12 months | ☐ | ☐ | ☐ |  |
| Work order backlog reviewed — no safety-critical items deferred > 30 days | ☐ | ☐ | ☐ |  |

🏢  SECTION 9 — BUILDING ENVELOPE & THERMAL LOAD ASSESSMENT

| Item / Audit Point | Pass | Fail | N/A | Notes / Findings |
| --- | --- | --- | --- | --- |
| Building load calculation available (ACCA Manual J or approved equivalent) | ☐ | ☐ | ☐ |  |
| Equipment sizing matches calculated load — no gross over/undersizing found | ☐ | ☐ | ☐ |  |
| Roof insulation R-value documented and meets current IECC requirements | ☐ | ☐ | ☐ |  |
| Wall insulation verified — thermal bridging locations identified | ☐ | ☐ | ☐ |  |
| Windows — U-factor and SHGC meet IECC requirements for climate zone | ☐ | ☐ | ☐ |  |
| Air sealing completed — blower door test result on file | ☐ | ☐ | ☐ |  |
| Vapor barriers installed correctly for climate zone | ☐ | ☐ | ☐ |  |
| Thermal imaging survey performed to identify envelope deficiencies | ☐ | ☐ | ☐ |  |
| Infiltration controlled — no major gaps around penetrations or exterior doors | ☐ | ☐ | ☐ |  |
| Solar shading devices operational (blinds, overhangs, window films) | ☐ | ☐ | ☐ |  |
| Internal heat loads documented — plug loads, lighting, occupancy density | ☐ | ☐ | ☐ |  |
| Lighting systems upgraded to LED — cooling load impact calculated | ☐ | ☐ | ☐ |  |

✅  SECTION 10 — COMMISSIONING & CODE COMPLIANCE REVIEW

| Item / Audit Point | Pass | Fail | N/A | Notes / Findings |
| --- | --- | --- | --- | --- |
| Original commissioning report available and on file | ☐ | ☐ | ☐ |  |
| Retrocommissioning (RCx) completed within last 5 years | ☐ | ☐ | ☐ |  |
| Test and balance (TAB) report available and current | ☐ | ☐ | ☐ |  |
| Permit history reviewed — all HVAC work permitted and inspected | ☐ | ☐ | ☐ |  |
| Equipment meets current SEER2 / EER2 minimum efficiency standards | ☐ | ☐ | ☐ |  |
| Refrigerant compliant with current and pending EPA AIM Act phasedown schedule | ☐ | ☐ | ☐ |  |
| Hazardous materials survey complete for older equipment (asbestos, lead) | ☐ | ☐ | ☐ |  |
| Arc flash study completed and warning labels affixed (NFPA 70E) | ☐ | ☐ | ☐ |  |
| All equipment labeled per NEC and local code requirements | ☐ | ☐ | ☐ |  |
| As-built drawings available, current, and accurate | ☐ | ☐ | ☐ |  |
| O&M manuals on site and accessible to maintenance staff | ☐ | ☐ | ☐ |  |
| Emergency contact list and equipment shut-off locations posted | ☐ | ☐ | ☐ |  |

📊  SECTION 11 — AUDIT SCORING SUMMARY

| Audit Category | Max Points | Points Earned | Finding Summary |
| --- | --- | --- | --- |
| Section 3 — Energy Performance | 25 |  |  |
| Section 4 — Mechanical Systems | 20 |  |  |
| Section 5 — Controls & BAS | 15 |  |  |
| Section 6 — IAQ & Ventilation Compliance | 15 |  |  |
| Section 7 — Refrigerant Compliance | 10 |  |  |
| Section 8 — Preventive Maintenance Program | 10 |  |  |
| Section 9 — Building Envelope & Thermal Load | 5 |  |  |
| Section 10 — Commissioning & Code Compliance | 10 |  |  |
| TOTAL SCORE | 100 |  |  |

Score Interpretation: 90–100 = Excellent 75–89 = Good 60–74 = Acceptable 45–59 = Deficient < 45 = Critical Overall Audit Score: _____ / 100 Audit Grade: ☐ Excellent ☐ Good ☐ Acceptable ☐ Deficient ☐ Critical

🚨  SECTION 12 — PRIORITY FINDINGS & RECOMMENDATIONS

| Priority | Finding Description | Est. Cost | Est. Savings/Yr | Recommended Action |
| --- | --- | --- | --- | --- |
| P1 | [Immediate — Safety or Code Deficiency] | $ | $ |  |
| P1 | [Immediate — Safety or Code Deficiency] | $ | $ |  |
| P2 | [Short Term (< 90 days) — Operational] | $ | $ |  |
| P2 | [Short Term (< 90 days) — Operational] | $ | $ |  |
| P2 | [Short Term (< 90 days) — Operational] | $ | $ |  |
| P3 | [Long Term — Capital Improvement] | $ | $ |  |
| P3 | [Long Term — Capital Improvement] | $ | $ |  |
| P3 | [Long Term — Capital Improvement] | $ | $ |  |

✍️  SECTION 13 — AUTHORIZATION & SIGNATURES

| Lead Auditor (Print) | Lead Auditor Signature | Audit Date |
| --- | --- | --- |

| Co-Auditor / Witness (Print) | Co-Auditor Signature | Date |
| --- | --- | --- |

| Facility Manager / Owner Rep (Print) | Owner / Rep Signature | Date Accepted |
| --- | --- | --- |

Report Certification: I certify that this audit was conducted in accordance with referenced standards and that all findings accurately represent conditions observed at the time of audit.