📋 SECTION 1 — PROJECT & EQUIPMENT INFORMATION

Project Details

| Commissioning Report No. | _________________________________ |
| --- | --- |
| Date of Commissioning | _________________________________ |
| Commissioning Technician | _________________________________ |
| Supervising Engineer | _________________________________ |
| Project / Job Number | _________________________________ |
| Site / Facility Name | _________________________________ |
| Building / Location | _________________________________ |
| Floor / Zone / AHU # | _________________________________ |
| Owner / Client Name | _________________________________ |
| General Contractor | _________________________________ |

Equipment Identification

| Equipment Tag / ID | _________________________________ |
| --- | --- |
| Equipment Type | _________________________________ |
| Manufacturer | _________________________________ |
| Model Number | _________________________________ |
| Serial Number | _________________________________ |
| Nominal Cooling Capacity (Tons) | _________________________________ |
| Nominal Heating Capacity (BTU/hr) | _________________________________ |
| Refrigerant Type | _________________________________ |
| Electrical Supply (V / Ph / Hz) | _________________________________ |
| Installation Date | _________________________________ |
| Warranty Start Date | _________________________________ |
| Startup Performed By | _________________________________ |

🔍 SECTION 2 — PRE-COMMISSIONING VERIFICATION

⚠ All pre-commissioning checks must be completed and documented before energizing equipment.

Site & Installation Readiness

| Commissioning Item | Pass | Fail | N/A | Notes / Corrective Action |
| --- | --- | --- | --- | --- |
| Equipment installed in correct location per project drawings | ☐ | ☐ | ☐ |  |
| Adequate clearances maintained on all sides (per manufacturer spec) | ☐ | ☐ | ☐ |  |
| Unit is level and plumb; vibration isolation pads or spring isolators installed | ☐ | ☐ | ☐ |  |
| Roof curb sealed and flashed correctly (rooftop units) | ☐ | ☐ | ☐ |  |
| Equipment anchored and secured per seismic / wind load requirements | ☐ | ☐ | ☐ |  |
| All shipping bolts, brackets, and restraints removed | ☐ | ☐ | ☐ |  |
| Packaging materials, desiccants, and transit plugs removed | ☐ | ☐ | ☐ |  |
| Equipment nameplate data matches submittal / schedule | ☐ | ☐ | ☐ |  |
| All access panels and covers in place | ☐ | ☐ | ☐ |  |

Mechanical Connections

| Commissioning Item | Pass | Fail | N/A | Notes / Corrective Action |
| --- | --- | --- | --- | --- |
| Supply and return ductwork connected and sealed (no visible leaks) | ☐ | ☐ | ☐ |  |
| Duct connections properly supported — no strain on unit collars | ☐ | ☐ | ☐ |  |
| Condensate drain piped to approved discharge point with trap installed | ☐ | ☐ | ☐ |  |
| Condensate drain tested — flows freely with no blockage | ☐ | ☐ | ☐ |  |
| Refrigerant line set properly supported and insulated | ☐ | ☐ | ☐ |  |
| Service valves open — both liquid and suction lines | ☐ | ☐ | ☐ |  |
| Filter(s) installed — correct size, quantity, and MERV rating | ☐ | ☐ | ☐ |  |
| Outdoor air intake / exhaust connections complete | ☐ | ☐ | ☐ |  |
| Fresh air damper / economizer linkage connected and operable | ☐ | ☐ | ☐ |  |

⚡ SECTION 3 — ELECTRICAL & CONTROLS VERIFICATION

Power Supply & Wiring

| Commissioning Item | Pass | Fail | N/A | Notes / Corrective Action |
| --- | --- | --- | --- | --- |
| Dedicated circuit breaker / disconnect installed and labeled | ☐ | ☐ | ☐ |  |
| Supply voltage verified at disconnect — within ±10% of nameplate | ☐ | ☐ | ☐ |  |
| Voltage imbalance measured and within 2% (3-phase units) | ☐ | ☐ | ☐ |  |
| Wire size and overcurrent protection matches MCA / MOCP on nameplate | ☐ | ☐ | ☐ |  |
| All field wiring connections tight — no loose lugs or terminals | ☐ | ☐ | ☐ |  |
| Ground wire landed at unit ground lug | ☐ | ☐ | ☐ |  |
| High-voltage and low-voltage wiring in separate conduits | ☐ | ☐ | ☐ |  |
| Conduit connections sealed and weatherproofed (outdoor units) | ☐ | ☐ | ☐ |  |
| Disconnect lockout/tagout capability confirmed | ☐ | ☐ | ☐ |  |

Controls, Thermostat & BAS

| Commissioning Item | Pass | Fail | N/A | Notes / Corrective Action |
| --- | --- | --- | --- | --- |
| Thermostat / controller installed per wiring diagram | ☐ | ☐ | ☐ |  |
| Control wiring verified — no shorts, opens, or crossed wires | ☐ | ☐ | ☐ |  |
| BAS / DDC points wired and communication link confirmed | ☐ | ☐ | ☐ |  |
| Sensor calibration verified: space temp, supply temp, return temp | ☐ | ☐ | ☐ |  |
| Outdoor air temperature sensor installed and reading correctly | ☐ | ☐ | ☐ |  |
| Humidity sensors calibrated (if applicable) | ☐ | ☐ | ☐ |  |
| CO2 / DCV sensors calibrated and functional (if applicable) | ☐ | ☐ | ☐ |  |
| Scheduling configured in controller / BAS | ☐ | ☐ | ☐ |  |
| Setpoints entered per design sequences of operation | ☐ | ☐ | ☐ |  |
| Occupied / unoccupied modes tested and functional | ☐ | ☐ | ☐ |  |
| Demand-controlled ventilation sequence tested (if applicable) | ☐ | ☐ | ☐ |  |
| Remote monitoring / fault reporting confirmed operational | ☐ | ☐ | ☐ |  |

❄ SECTION 4 — REFRIGERATION SYSTEM COMMISSIONING

⚠ Only EPA 608 certified technicians may handle refrigerants. Record all refrigerant additions on a refrigerant log.

Refrigerant Circuit Pre-Start

| Commissioning Item | Pass | Fail | N/A | Notes / Corrective Action |
| --- | --- | --- | --- | --- |
| Factory refrigerant charge verified (pre-charged unit) or field-charged | ☐ | ☐ | ☐ |  |
| Leak check performed — no leaks detected (electronic leak detector) | ☐ | ☐ | ☐ |  |
| Refrigerant type confirmed matches unit label and project spec | ☐ | ☐ | ☐ |  |
| Sight glass clear — no bubbles under normal operating conditions | ☐ | ☐ | ☐ |  |
| Oil level confirmed (if accessible) | ☐ | ☐ | ☐ |  |
| Crankcase heater energized minimum 8 hours prior to startup | ☐ | ☐ | ☐ |  |
| High/low pressure switches checked — set to manufacturer limits | ☐ | ☐ | ☐ |  |

Refrigeration Circuit Measurements

| Parameter | Design | Measured | Unit | Tolerance | Status | Notes |
| --- | --- | --- | --- | --- | --- | --- |
| Suction Pressure (Low Side) |  |  |  |  |  |  |
| Discharge Pressure (High Side) |  |  |  |  |  |  |
| Suction Line Temperature |  |  |  |  |  |  |
| Liquid Line Temperature |  |  |  |  |  |  |
| Superheat at Evaporator Outlet |  |  |  |  |  |  |
| Subcooling at Condenser Outlet |  |  |  |  |  |  |
| Compressor Discharge Temp |  |  |  |  |  |  |
| Saturated Suction Temp (SST) |  |  |  |  |  |  |
| Saturated Discharge Temp (SDT) |  |  |  |  |  |  |
| Refrigerant Charge Added (lbs) |  |  |  |  |  |  |

💨 SECTION 5 — AIRSIDE PERFORMANCE & TAB

ℹ Test and Balance (TAB) data should be cross-referenced with the certified TAB report where required by contract.

Fan & Airflow Measurements

| Parameter | Design | Measured | Unit | Tolerance | Status | Notes |
| --- | --- | --- | --- | --- | --- | --- |
| Supply Airflow — Total (CFM) |  |  |  |  |  |  |
| Return Airflow — Total (CFM) |  |  |  |  |  |  |
| Outside Air CFM |  |  |  |  |  |  |
| Exhaust / Relief Air CFM |  |  |  |  |  |  |
| Supply Fan RPM |  |  |  |  |  |  |
| Supply Fan Amp Draw (Actual) |  |  |  |  |  |  |
| Supply Fan Amp Draw (Nameplate) |  |  |  |  |  |  |
| Return Fan Amp Draw (if applicable) |  |  |  |  |  |  |
| External Static Pressure |  |  |  |  |  |  |
| Supply Duct Static Pressure |  |  |  |  |  |  |
| Return Duct Static Pressure |  |  |  |  |  |  |
| Filter Pressure Drop |  |  |  |  |  |  |

Air Temperature Measurements

| Parameter | Design | Measured | Unit | Tolerance | Status | Notes |
| --- | --- | --- | --- | --- | --- | --- |
| Supply Air Temperature |  |  |  |  |  |  |
| Return Air Temperature |  |  |  |  |  |  |
| Delta T — Cooling Mode |  |  |  |  |  |  |
| Delta T — Heating Mode |  |  |  |  |  |  |
| Outdoor Air Temperature |  |  |  |  |  |  |
| Mixed Air Temperature |  |  |  |  |  |  |
| Discharge Air Temperature |  |  |  |  |  |  |
| Space Temperature (Avg) |  |  |  |  |  |  |

Economizer & Ventilation

| Commissioning Item | Pass | Fail | N/A | Notes / Corrective Action |
| --- | --- | --- | --- | --- |
| Economizer damper opens fully when conditions met | ☐ | ☐ | ☐ |  |
| Economizer damper closes fully in mechanical cooling mode | ☐ | ☐ | ☐ |  |
| Minimum OA damper position set per design CFM | ☐ | ☐ | ☐ |  |
| Enthalpy or dry-bulb changeover control verified (if applicable) | ☐ | ☐ | ☐ |  |
| Barometric relief / power exhaust operational | ☐ | ☐ | ☐ |  |
| CO2 DCV reset verified (if applicable) | ☐ | ☐ | ☐ |  |

🛡 SECTION 6 — SAFETY DEVICES & INTERLOCKS

⚠ Verify all safety shutdowns trip correctly. Document trip value and reset value for each device.

Refrigeration Safety Controls

| Commissioning Item | Pass | Fail | N/A | Notes / Corrective Action |
| --- | --- | --- | --- | --- |
| High-pressure cutout — tested and trips at set point | ☐ | ☐ | ☐ |  |
| Low-pressure cutout — tested and trips at set point | ☐ | ☐ | ☐ |  |
| Compressor overload protection — functional | ☐ | ☐ | ☐ |  |
| Anti-short-cycle timer — minimum 3-minute off-delay confirmed | ☐ | ☐ | ☐ |  |
| Low-ambient lockout (heating / cooling mode) — verified | ☐ | ☐ | ☐ |  |
| Freeze stat / low-limit stat — trips at set temperature | ☐ | ☐ | ☐ |  |
| Condenser fan cycling control — stages correctly | ☐ | ☐ | ☐ |  |

Electrical & Mechanical Safety

| Commissioning Item | Pass | Fail | N/A | Notes / Corrective Action |
| --- | --- | --- | --- | --- |
| Phase loss / phase reversal protection functional (3-phase) | ☐ | ☐ | ☐ |  |
| Motor overloads set correctly and tested for each motor | ☐ | ☐ | ☐ |  |
| Supply fan belt tension correct (belt-drive units) — no slip or squeal | ☐ | ☐ | ☐ |  |
| All access door interlocks functional — unit shuts off when opened | ☐ | ☐ | ☐ |  |
| Smoke detector / fire stat — trips unit and returns correct alarm | ☐ | ☐ | ☐ |  |
| Dirty filter switch / differential pressure switch functional | ☐ | ☐ | ☐ |  |
| Condensate overflow float switch tested — shuts unit off on high water | ☐ | ☐ | ☐ |  |
| Gas valve safety interlocks (gas heating) — functional | ☐ | ☐ | ☐ |  |
| Ignition sequence tested — lockout on failed ignition | ☐ | ☐ | ☐ |  |
| Rollout and limit switches tested (gas heating) | ☐ | ☐ | ☐ |  |

Safety Device Set Points

| Safety Device | Design Set Point | Actual Trip Point | Reset Point | Status |
| --- | --- | --- | --- | --- |
| High Pressure Cutout |  |  |  |  |
| Low Pressure Cutout |  |  |  |  |
| Freeze Stat / Low Limit |  |  |  |  |
| Condensate Float Switch |  |  |  |  |
| Smoke / Fire Stat |  |  |  |  |
| Supply Fan Overload |  |  |  |  |
| Compressor Overload |  |  |  |  |

✅ SECTION 7 — FINAL FUNCTIONAL PERFORMANCE TEST

Cooling Mode Functional Test

| Commissioning Item | Pass | Fail | N/A | Notes / Corrective Action |
| --- | --- | --- | --- | --- |
| Unit enters cooling mode on call from thermostat / BAS | ☐ | ☐ | ☐ |  |
| Compressor(s) stage on in correct sequence | ☐ | ☐ | ☐ |  |
| Condenser fan(s) operate correctly at all stages | ☐ | ☐ | ☐ |  |
| Supply air temperature achieves design setpoint within 15 minutes | ☐ | ☐ | ☐ |  |
| Space temperature reaches setpoint within design runtime | ☐ | ☐ | ☐ |  |
| Unit stages off cleanly — no short cycling observed | ☐ | ☐ | ☐ |  |
| Compressor off-delay / anti-short-cycle timer functions | ☐ | ☐ | ☐ |  |

Heating Mode Functional Test

| Commissioning Item | Pass | Fail | N/A | Notes / Corrective Action |
| --- | --- | --- | --- | --- |
| Unit enters heating mode on call from thermostat / BAS | ☐ | ☐ | ☐ |  |
| Heat stages / gas valve / heat pump stages in correct sequence | ☐ | ☐ | ☐ |  |
| Supply air temperature achieves heating design setpoint | ☐ | ☐ | ☐ |  |
| Space temperature reaches setpoint within design runtime | ☐ | ☐ | ☐ |  |
| Heating lockout above outdoor setpoint functional (heat pump) | ☐ | ☐ | ☐ |  |
| Auxiliary / emergency heat activates correctly (heat pump) | ☐ | ☐ | ☐ |  |
| Defrost cycle initiates and terminates correctly (heat pump) | ☐ | ☐ | ☐ |  |

Ventilation & Dehumidification

| Commissioning Item | Pass | Fail | N/A | Notes / Corrective Action |
| --- | --- | --- | --- | --- |
| Fan-only mode (ventilation) operates independently of cooling/heating | ☐ | ☐ | ☐ |  |
| Minimum ventilation maintained during all occupied modes | ☐ | ☐ | ☐ |  |
| Dehumidification mode functional — space RH reaches setpoint | ☐ | ☐ | ☐ |  |
| Hot gas reheat / dehumidification sequence correct (if applicable) | ☐ | ☐ | ☐ |  |
| No condensation on supply diffusers at design conditions | ☐ | ☐ | ☐ |  |

Overall Commissioning Performance Summary

| Section | Items Checked | Pass | Fail | N/A | Overall Status |
| --- | --- | --- | --- | --- | --- |
| Pre-Commissioning & Site |  |  |  |  |  |
| Mechanical Installation |  |  |  |  |  |
| Electrical & Controls |  |  |  |  |  |
| Refrigeration System |  |  |  |  |  |
| Airside Performance |  |  |  |  |  |
| Controls & BAS |  |  |  |  |  |
| Safety Devices |  |  |  |  |  |
| Final Functional Test |  |  |  |  |  |

Outstanding Items / Deficiencies

| # | Deficiency Description | Responsible Party | Target Resolution Date |
| --- | --- | --- | --- |
| 1 |  |  |  |
| 2 |  |  |  |
| 3 |  |  |  |
| 4 |  |  |  |
| 5 |  |  |  |

📁 SECTION 8 — DOCUMENTATION & SIGN-OFF

Documents Provided to Owner / Facility Manager

| Commissioning Item | Pass | Fail | N/A | Notes / Corrective Action |
| --- | --- | --- | --- | --- |
| Manufacturer's start-up / commissioning report | ☐ | ☐ | ☐ |  |
| Warranty registration certificate | ☐ | ☐ | ☐ |  |
| Operation & Maintenance (O&M) manuals | ☐ | ☐ | ☐ |  |
| Wiring diagrams and controls schematics (as-built) | ☐ | ☐ | ☐ |  |
| TAB report (if applicable) | ☐ | ☐ | ☐ |  |
| Refrigerant addition log | ☐ | ☐ | ☐ |  |
| BAS programming documentation and point list | ☐ | ☐ | ☐ |  |
| Filter replacement schedule and recommended spare parts list | ☐ | ☐ | ☐ |  |
| Emergency shutdown and restart procedures | ☐ | ☐ | ☐ |  |
| Preventive maintenance (PM) schedule | ☐ | ☐ | ☐ |  |

ℹ Commissioning is considered complete only when all Pass/Fail items are resolved and all signatures below are obtained.

Commissioning Technician Sign-Off

| Commissioning Technician Name: ___________________________ Title: ___________________________ Company: ________________________ Signature: ______________________ Date: ___________________________ | Lead / Senior Technician (if applicable) Name: ___________________________ Title: ___________________________ Company: ________________________ Signature: ______________________ Date: ___________________________ |
| --- | --- |

Engineer of Record / Cx Agent

| Commissioning Agent / Engineer Name: ___________________________ Title: ___________________________ Company: ________________________ Signature: ______________________ Date: ___________________________ | Mechanical Engineer of Record Name: ___________________________ Title: ___________________________ Company: ________________________ Signature: ______________________ Date: ___________________________ |
| --- | --- |

Owner / Facility Acceptance

| Facility Manager / Owner Representative Name: ___________________________ Title: ___________________________ Company: ________________________ Signature: ______________________ Date: ___________________________ | Authorizing Executive (if required) Name: ___________________________ Title: ___________________________ Company: ________________________ Signature: ______________________ Date: ___________________________ |
| --- | --- |

Final Commissioning Disposition

Final Commissioning Status: ☐ COMMISSIONED — All items pass; unit accepted for occupancy ☐ CONDITIONALLY COMMISSIONED — Minor items outstanding; see deficiency log ☐ FAILED — Unit cannot be accepted; re-commissioning required Comments: _______________________________________________________________________________ _______________________________________________________________________________ _______________________________________________________________________________