HVAC SEQUENCE OF OPERATIONS This document defines the intended control logic, operating modes, setpoints, alarms, and I/O for the HVAC system described herein. It shall be used as the basis for programming, commissioning, and owner training.

📋  SECTION 1 — PROJECT & DOCUMENT INFORMATION

| Project Name: ________________________ | Work Order / Job #: ________________________ |
| --- | --- |
| Project Address: ________________________ | City / State / ZIP: ________________________ |
| System Description: ________________________ | Equipment Tag / ID: ________________________ |
| Controls Engineer: ________________________ | Company / Firm: ________________________ |
| Document Revision: ________________________ | Revision Date: ________________________ |
| Approved By: ________________________ | Approval Date: ________________________ |

🏗️  SECTION 2 — SYSTEM OVERVIEW

| Attribute | Description |
| --- | --- |
| Equipment Type | [e.g., Rooftop Unit / AHU / Split System / Chiller Plant] |
| Manufacturer / Model | ________________________ |
| Capacity — Cooling | ________________________ Tons |
| Capacity — Heating | ________________________ MBH / kW |
| Airflow — Design | ________________________ CFM |
| Refrigerant Type | ________________________ |
| Control System | [e.g., DDC / BACnet / Proprietary Thermostat] |
| BAS Integration | [Yes / No — Protocol: BACnet MS/TP ¦ BACnet IP ¦ Modbus ¦ N2] |
| Zoning | [Single Zone / Multi-Zone VAV / Constant Volume] |
| Economizer | [Yes — Type: Differential Dry-Bulb ¦ Enthalpy ¦ Fixed OA] / No |

ℹ️ NOTE: Complete all highlighted fields with project-specific equipment data before issuing for construction or commissioning.

⚙️  SECTION 3 — OPERATING MODES & CONTROL LOGIC

3A — Cooling Mode

| # | Condition / State | Action / Output | Setpoint / Value | Notes |
| --- | --- | --- | --- | --- |
| 1 | Space temp > Cooling setpoint | Compressor stage 1 energizes; supply fan at design CFM | 75 °F | Verify condenser fan operation |
| 2 | Space temp > Cooling setpoint + 1°F | Compressor stage 2 energizes (if applicable) | 76 °F | 2-stage only |
| 3 | Economizer conditions met | OA damper modulates open; compressor off if adequate free cooling | Δh or ΔT | Per economizer strategy |
| 4 | Space temp ≤ Cooling setpoint − 0.5°F | Compressor de-energizes; fan continues through off-delay | 74.5 °F | 2-min off-delay typical |
| 5 | Cooling satisfied | Supply fan returns to minimum position or off per schedule | — |  |

3B — Heating Mode

| # | Condition / State | Action / Output | Setpoint / Value | Notes |
| --- | --- | --- | --- | --- |
| 1 | Space temp < Heating setpoint | Heating stage 1 energizes (gas / electric / HP reversing valve) | 70 °F | Verify ignition / aux heat |
| 2 | Space temp < Heating setpoint − 1°F | Heating stage 2 / supplemental heat energizes | 69 °F | Staged or modulating |
| 3 | Space temp ≥ Heating setpoint + 0.5°F | Heating de-energizes; supply fan continues through off-delay | 70.5 °F | 1-min off-delay |
| 4 | Heating satisfied | Supply fan off or returns to minimum position | — |  |

3C — Ventilation / Fan Operation

| # | Condition / State | Action / Output | Setpoint / Value | Notes |
| --- | --- | --- | --- | --- |
| 1 | Occupied schedule active | Supply fan starts at design CFM; OA damper opens to minimum | Design CFM | Per TAB report |
| 2 | Unoccupied schedule active | Fan off (or cycles on temp deviation); OA damper fully closed | — | Setup/setback mode |
| 3 | CO₂ > DCV setpoint | OA damper modulates open; fan speed increases if VFD equipped | 1,000 ppm | DCV if applicable |
| 4 | CO₂ ≤ DCV setpoint − 100 ppm | OA damper returns to minimum; fan speed returns to design | 900 ppm |  |
| 5 | Manual override active | Fan forced ON; OA damper at minimum; all modes override | Operator | BAS or local override |

3D — Economizer Mode

| # | Condition / State | Action / Output | Setpoint / Value | Notes |
| --- | --- | --- | --- | --- |
| 1 | OA dry-bulb < RAT − 2°F (or low enthalpy) | Economizer mode enabled; OA damper modulates for supply air Tsp | 55 °F SAT | Enthalpy if sensor fitted |
| 2 | Mechanical cooling required | Compressor stages per call for cooling; OA at minimum | Per SAT |  |
| 3 | OA conditions exceed limits | Economizer disabled; OA damper returns to minimum position | — | High OA temp or enthalpy |
| 4 | High-limit shutoff | OA damper fully closes; alarm generated | Per ASHRAE 90.1 |  |

3E — Dehumidification Mode (if applicable)

| # | Condition / State | Action / Output | Setpoint / Value | Notes |
| --- | --- | --- | --- | --- |
| 1 | RH > Dehumidification setpoint | Cooling operates; reheat energizes to maintain space temp setpoint | 60 % RH | If reheat provided |
| 2 | RH ≤ Dehumidification setpoint − 5% | Reheat de-energizes; system returns to normal cooling mode | 55 % RH |  |
| 3 | RH sensor fault | System defaults to cooling mode; alarm generated | — | Fail-safe |

⚠️  All modes are subject to safety interlock override. Smoke detector trip shall shut down supply fan and close OA damper regardless of operating mode.

🎛️  SECTION 4 — SETPOINTS REFERENCE TABLE

| Parameter | Default Setpoint | Adjustable Range | Unit | Notes / Authority |
| --- | --- | --- | --- | --- |
| Cooling Setpoint — Occupied | 74 | 70 – 78 | °F | Adjustable at thermostat / BAS |
| Cooling Setpoint — Unoccupied | 85 | 80 – 90 | °F | Setup setback |
| Heating Setpoint — Occupied | 70 | 65 – 74 | °F | Adjustable at thermostat / BAS |
| Heating Setpoint — Unoccupied | 60 | 55 – 65 | °F | Setback |
| Supply Air Temperature — Cooling | 55 | 52 – 60 | °F | Discharge air controller |
| Supply Air Temperature — Heating | 90 | 80 – 120 | °F | Limit per mfr |
| Economizer High-Limit (Dry-Bulb) | 65 | 60 – 70 | °F OAT | ASHRAE 90.1 Table 6.5.1.1 |
| Economizer High-Limit (Enthalpy) | 28 | 26 – 30 | BTU/lb | If enthalpy economizer |
| Minimum OA — Design | Per TAB | — | CFM | Per ASHRAE 62.1 / design |
| CO₂ Setpoint — DCV | 1,000 | 800 – 1,200 | ppm | If DCV equipped |
| Dehumidification Setpoint | 60 | 50 – 65 | % RH | If RH sensor installed |
| Supply Fan Speed — Occupied | 100 | 80 – 100 | % speed | VFD if applicable |
| Supply Fan Speed — Unoccupied | 0 | 0 – 30 | % speed | Off or low-speed purge |
| Compressor Lockout — Low OAT | 45 | 40 – 55 | °F | Protect compressor |
| Compressor Lockout — High OAT | 115 | 110 – 125 | °F | Protect compressor |
| Heating Lockout — High OAT | 65 | 60 – 70 | °F | No heat above this OAT |
| Cooling Off-Delay | 120 | 60 – 300 | Sec | Prevent short-cycling |
| Heating Off-Delay | 60 | 30 – 180 | Sec | Purge cycle |

📌 NOTE: Setpoints shall be adjusted by the commissioning agent during startup and confirmed with the owner. All setpoints are programmable via the BAS or local controller interface.

🚨  SECTION 5 — ALARMS & FAULT MANAGEMENT

| Alarm / Fault | Trigger Condition | System Response | Priority | Reset Method |
| --- | --- | --- | --- | --- |
| High Space Temperature | Space temp > 85 °F for 15 min | Alert; cooling forced on; notify BAS | High | Auto on temp drop |
| Low Space Temperature | Space temp < 55 °F for 10 min | Alert; heating forced on; freeze protection | High | Auto on temp rise |
| Supply Air High Limit | SAT > 120 °F | Heating disabled; alarm latched | High | Manual reset |
| Supply Air Low Limit | SAT < 45 °F for 5 min | Freeze stat: fan off; OA damper closed; alarm | High | Manual reset |
| Compressor Fault | Compressor trip / high-pressure cutout | Compressor off; alarm; backup stage if avail. | High | Manual reset |
| Dirty Filter | Filter DP switch > threshold | Alert only; schedule maintenance | Medium | Auto clear after reset |
| Fan Failure | Proof switch open after 30 sec | Unit shutdown; alarm latched | High | Manual reset |
| Low Refrigerant | Suction pressure < 60 PSIG (R-410A) | Compressor off; alert technician | High | Manual reset |
| Communication Loss | No BAS heartbeat > 15 min | Unit goes to stand-alone local schedule | Medium | Auto on reconnect |
| OA Damper Fault | Damper feedback ≠ command for 5 min | Damper defaults closed; alert | Medium | Manual reset |
| High Indoor Humidity | RH > 70 % for 20 min | Cooling / dehumid mode forced; alert | Medium | Auto on RH drop |
| CO₂ High Alarm | CO₂ > 1,200 ppm for 10 min | OA damper fully open; alert occupants | Medium | Auto on CO₂ drop |

⚠️  High-priority alarms latch and require manual reset at the controller or BAS. All alarms shall be annunciated at the BAS and optionally via email/text notification to the facility manager.

🔌  SECTION 6 — POINTS LIST & I/O SCHEDULE

Analog Inputs (AI)  |  Digital Inputs (DI)  |  Analog Outputs (AO)  |  Digital Outputs (DO)

| Point Name / Tag | Signal Type | I / O | Range / States | Controller Point | Notes |
| --- | --- | --- | --- | --- | --- |
| Space Temperature Sensor | AI (0-10V) | Input | 32–122 °F | AI-1 | Zone thermostat / remote sensor |
| Supply Air Temp Sensor | AI (0-10V) | Input | 32–122 °F | AI-2 | Discharge air sensor |
| Return Air Temp Sensor | AI (0-10V) | Input | 32–122 °F | AI-3 | Return duct sensor |
| OA Temperature Sensor | AI (0-10V) | Input | −40–122 °F | AI-4 | Economizer / lockout |
| OA Enthalpy Sensor | AI (4-20mA) | Input | 0–100 BTU/lb | AI-5 | If enthalpy economizer |
| Supply Fan Proof (Status) | DI (Dry) | Input | On / Off | DI-1 | Airflow proving switch |
| Filter DP Switch | DI (Dry) | Input | Open/Closed | DI-2 | High-DP = dirty filter |
| Smoke Detector — Supply | DI (Dry) | Input | Normal/Alarm | DI-3 | Fan interlock |
| High-Pressure Cutout | DI (Dry) | Input | Normal/Trip | DI-4 | Compressor protection |
| Low-Pressure Cutout | DI (Dry) | Input | Normal/Trip | DI-5 | Compressor protection |
| CO₂ Sensor | AI (0-10V) | Input | 0–2,000 ppm | AI-6 | If DCV equipped |
| RH Sensor — Space | AI (0-10V) | Input | 0–100% RH | AI-7 | If dehumidification |
| Occupancy Sensor | DI (Dry) | Input | Occ / Unocc | DI-6 | Override schedule |
| Compressor Stage 1 | DO (24VAC) | Output | On / Off | DO-1 | Contactor / IFC signal |
| Compressor Stage 2 | DO (24VAC) | Output | On / Off | DO-2 | 2-stage only |
| Reversing Valve (Heat Pump) | DO (24VAC) | Output | On / Off | DO-3 | O or B per mfr |
| Heating Stage 1 | DO (24VAC) | Output | On / Off | DO-4 | Gas valve / heat strip |
| Heating Stage 2 | DO (24VAC) | Output | On / Off | DO-5 | Aux heat |
| Supply Fan Enable | DO (24VAC) | Output | On / Off | DO-6 | Fan contactor |
| Supply Fan Speed (VFD) | AO (0-10V) | Output | 0–100% | AO-1 | If VFD equipped |
| OA / Economizer Damper | AO (0-10V) | Output | 0–100% open | AO-2 | Spring-return actuator |
| Reheat / Zone Valve | AO (0-10V) | Output | 0–100% open | AO-3 | If modulating |
| Alarm Output | DO (Dry) | Output | Normal/Alarm | DO-7 | BAS / annunciator |

📌 NOTE: Confirm point addresses and wiring terminations against the controller submittal and as-built wiring diagrams. Signal types may vary by controller manufacturer.

📅  SECTION 7 — OCCUPANCY SCHEDULE

| Day | Occupied Start | Occupied End | Setback Clg | Setback Htg | Notes |
| --- | --- | --- | --- | --- | --- |
| Monday | 6:00 AM | 6:00 PM | 85 °F | 60 °F |  |
| Tuesday | 6:00 AM | 6:00 PM | 85 °F | 60 °F |  |
| Wednesday | 6:00 AM | 6:00 PM | 85 °F | 60 °F |  |
| Thursday | 6:00 AM | 6:00 PM | 85 °F | 60 °F |  |
| Friday | 6:00 AM | 6:00 PM | 85 °F | 60 °F |  |
| Saturday | Unoccupied | — | 85 °F | 60 °F | Off / On-demand |
| Sunday | Unoccupied | — | 85 °F | 60 °F | Off / On-demand |

ℹ️ NOTE: Schedules shall be field-adjusted per owner operational requirements. Holiday schedules and exceptions shall be programmed separately in the BAS. Occupancy sensor override provides 2-hour extension.

📝  SECTION 8 — REVISION HISTORY

| Rev | Date | Author | Description of Change |
| --- | --- | --- | --- |
| A |  |  | Initial release |
| B |  |  |  |
| C |  |  |  |
| D |  |  |  |

✍️  SECTION 9 — REVIEW & APPROVAL

| Controls Engineer / Designer | Commissioning Agent | Owner / Facility Manager |
| --- | --- | --- |
| Signature ________________________ | Signature ________________________ | Signature ________________________ |
| Printed Name ________________________ | Printed Name ________________________ | Printed Name ________________________ |
| Company ________________________ | Company ________________________ | Company ________________________ |
| Date ________________________ | Date ________________________ | Date ________________________ |

This Sequence of Operations is a design document and must be reviewed against final submitted equipment and control submittals before programming.