HVAC EQUIPMENT STARTUP CHECKLIST Complete all sections in order. Record all measurements. Do not energize equipment until Pre-Startup safety checks are signed off.

📋  SECTION 1 — PROJECT & EQUIPMENT IDENTIFICATION

| Work Order #: ________________________ | Startup Date: ________________________ |
| --- | --- |
| Project Name: ________________________ | Project Address: ________________________ |
| Lead Technician: ________________________ | Helper / Assistant: ________________________ |
| Equipment Type: ________________________ | Equipment Tag / ID: ________________________ |
| Manufacturer: ________________________ | Model Number: ________________________ |
| Serial Number: ________________________ | Refrigerant Type: ________________________ |
| Nominal Capacity: ________________________ | Voltage / Phase / Hz: ________________________ |
| Controller / Thermostat: ________________________ | Permit / AHJ Inspector: ________________________ |

🛡️  SECTION 2 — PRE-STARTUP SAFETY CHECKLIST

⚠️  DO NOT energize equipment until ALL items in this section are verified and initialed by the lead technician.

| Inspection Item | Criteria / Action | Pass | Fail | N/A | Measured Value / Notes |
| --- | --- | --- | --- | --- | --- |
| Disconnect / Lockout | Main disconnect open and LOTO tag applied before work begins | ☐ | ☐ | ☐ |  |
| Area Clear of Personnel | No unauthorized personnel within equipment clearance zones | ☐ | ☐ | ☐ |  |
| PPE On | Safety glasses, gloves, and arc-flash PPE donned as required | ☐ | ☐ | ☐ |  |
| Equipment Not Damaged | Visual inspection complete — no shipping damage, dents, or debris | ☐ | ☐ | ☐ |  |
| Refrigerant Lines Capped | All service valve caps accounted for; Schrader cores verified | ☐ | ☐ | ☐ |  |
| Electrical Covers Secured | All wiring compartment covers in place before energizing | ☐ | ☐ | ☐ |  |
| Condensate System Clear | Drain pan clean; primary and secondary condensate lines open | ☐ | ☐ | ☐ |  |
| Air Filters Installed | Correct MERV rating; seated properly; access door latched | ☐ | ☐ | ☐ |  |
| Ductwork Connected & Sealed | Supply and return connections complete; no open takeoffs | ☐ | ☐ | ☐ |  |
| Gas Line Pressure Tested | Gas piping leak-tested with manometer; no detected leaks (if gas) | ☐ | ☐ | ☐ |  |
| Flue / Venting Complete | Vent pipe connected, supported, and terminated per code (if gas) | ☐ | ☐ | ☐ |  |
| Structural / Mounting Secure | Curb, pad, or hangers verified; vibration isolators installed | ☐ | ☐ | ☐ |  |
| Manufacturer Startup Form | Manufacturer's startup documentation on-site and ready to complete | ☐ | ☐ | ☐ |  |
| Refrigerant Log Ready | EPA-compliant refrigerant log form available for recording | ☐ | ☐ | ☐ |  |

📌 NOTE: Pre-startup safety sign-off required before proceeding to electrical energization. LOTO procedures must remain in place until electrical pre-checks are complete.

⚡  SECTION 3 — ELECTRICAL PRE-STARTUP CHECKS

| Inspection Item | Criteria / Action | Pass | Fail | N/A | Measured Value / Notes |
| --- | --- | --- | --- | --- | --- |
| Nameplate Voltage Verified | Confirm supply voltage matches equipment nameplate rating | ☐ | ☐ | ☐ |  |
| Breaker / Fuse Sizing | OCPD size per NEC and equipment nameplate MCA / MOCP | ☐ | ☐ | ☐ |  |
| Wire Gauge Verified | Conductor sizing per NEC 310 based on MCA; check for Al/Cu | ☐ | ☐ | ☐ |  |
| Torque Specifications Met | All power and control terminations torqued per mfr specs | ☐ | ☐ | ☐ |  |
| Ground Conductor Installed | Equipment grounding conductor present and terminated | ☐ | ☐ | ☐ |  |
| Control Wiring Verified | Low-voltage control wiring per wiring diagram; no shorts | ☐ | ☐ | ☐ |  |
| Contactor Contacts Inspected | Contact surfaces clean; no pitting or burning observed | ☐ | ☐ | ☐ |  |
| Capacitor Condition | Run/start capacitors checked for bulging or leakage | ☐ | ☐ | ☐ |  |
| Disconnect Within Line-of-Sight | Disconnect visible from unit per NEC 440.14 | ☐ | ☐ | ☐ |  |
| Interlock Circuits Verified | Safety interlock wiring (HP, LP, freeze stat, smoke) confirmed | ☐ | ☐ | ☐ |  |

📊  SECTION 4 — ELECTRICAL MEASUREMENTS

| Parameter | Measured | Unit | Spec / Range | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| Supply Voltage — L1 to L2 |  | VAC | ±5% nominal |  |  |
| Supply Voltage — L1 to L3 |  | VAC | ±5% nominal |  |  |
| Supply Voltage — L2 to L3 |  | VAC | ±5% nominal |  |  |
| Voltage Imbalance |  | % | ≤ 2% |  |  |
| Compressor RLA (Nameplate) |  | Amps | See nameplate |  |  |
| Compressor Amp Draw — L1 |  | Amps | ≤ RLA |  |  |
| Compressor Amp Draw — L2 |  | Amps | ≤ RLA |  |  |
| Compressor Amp Draw — L3 |  | Amps | ≤ RLA |  |  |
| Condenser Fan Motor — FLA (Nameplate) |  | Amps | See nameplate |  |  |
| Condenser Fan Amp Draw |  | Amps | ≤ FLA |  |  |
| Supply / Blower Motor — FLA |  | Amps | See nameplate |  |  |
| Blower Motor Amp Draw |  | Amps | ≤ FLA |  |  |
| Control Circuit Voltage |  | VAC | 24 VAC ± 10% |  |  |
| Static Capacitor — Start (µF) |  | µF | Per nameplate ±6% |  |  |
| Static Capacitor — Run (µF) |  | µF | Per nameplate ±6% |  |  |

📌 NOTE: Record measurements under steady-state operating conditions. Voltage imbalance > 2% requires investigation before completing startup.

❄️  SECTION 5 — REFRIGERATION SYSTEM CHECKS

| Inspection Item | Criteria / Action | Pass | Fail | N/A | Measured Value / Notes |
| --- | --- | --- | --- | --- | --- |
| Refrigerant Type Confirmed | Verify refrigerant type matches nameplate and EPA log | ☐ | ☐ | ☐ |  |
| Factory Charge Intact | Shipping valves open; no loss of holding charge detected | ☐ | ☐ | ☐ |  |
| Leak Test Performed | Electronic leak detector used; no leaks detected at fittings/welds | ☐ | ☐ | ☐ |  |
| Service Valves Open (Back-Seated) | Liquid and suction service valves fully open | ☐ | ☐ | ☐ |  |
| Sight Glass — Bubbles | Sight glass clear (no bubbles) under steady-state operation | ☐ | ☐ | ☐ |  |
| Sight Glass — Moisture Indicator | Moisture indicator green / dry (not yellow / wet) | ☐ | ☐ | ☐ |  |
| Filter-Drier Condition | Factory drier intact; replace if system was open to atmosphere | ☐ | ☐ | ☐ |  |
| Refrigerant Charge Method | Charge verified: weigh-in / subcooling / superheat method used | ☐ | ☐ | ☐ |  |
| Refrigerant Amount Logged | Pounds added/removed recorded on EPA refrigerant log | ☐ | ☐ | ☐ |  |
| Metering Device Type Confirmed | TXV / EXV / Orifice confirmed; bulb or electronic wiring secure | ☐ | ☐ | ☐ |  |

⚠️  All refrigerant handling must comply with EPA Section 608 regulations. Technician must hold valid EPA 608 Universal certification.

🌡️  SECTION 6 — REFRIGERANT MEASUREMENTS (3 Steady-State Readings)

ℹ️ NOTE: Allow minimum 15 minutes of operation before recording readings. Take 3 readings at 5-minute intervals. All three must be within spec before startup is considered complete.

| Parameter | Rdg 1 | Rdg 2 | Rdg 3 | Unit | Spec / Range | Status | Notes |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Suction Pressure |  |  |  | PSIG | Per mfr PT chart |  |  |
| Discharge Pressure |  |  |  | PSIG | Per mfr PT chart |  |  |
| Suction Saturation Temp |  |  |  | °F | Calculated from PSIG |  |  |
| Discharge Saturation Temp |  |  |  | °F | Calculated from PSIG |  |  |
| Suction Line Temp (6" from comp) |  |  |  | °F | Superheat target |  |  |
| Superheat — Calculated |  |  |  | °F | Per mfr spec |  |  |
| Liquid Line Temp (at cond out) |  |  |  | °F | Subcooling target |  |  |
| Subcooling — Calculated |  |  |  | °F | Per mfr spec |  |  |
| OA Dry-Bulb Temp |  |  |  | °F | Record ambient |  |  |
| Return Air Dry-Bulb |  |  |  | °F | Record actual |  |  |
| Supply Air Dry-Bulb |  |  |  | °F | Record actual |  |  |
| Delta-T (RAT − SAT) |  |  |  | °F | 16–22 °F typical |  |  |
| Return Air Wet-Bulb |  |  |  | °F | Record for psychrometrics |  |  |
| Supply Air Wet-Bulb |  |  |  | °F | Record for psychrometrics |  |  |

💨  SECTION 7 — AIRFLOW & MECHANICAL CHECKS

| Inspection Item | Criteria / Action | Pass | Fail | N/A | Measured Value / Notes |
| --- | --- | --- | --- | --- | --- |
| Belt Tension & Alignment | Belt tension per mfr spec; sheaves aligned; no glazing or cracking | ☐ | ☐ | ☐ |  |
| Blower Wheel Rotation | Blower rotates freely by hand; correct rotation confirmed at startup | ☐ | ☐ | ☐ |  |
| Condenser Fan Rotation | All condenser fan blades rotate freely; correct rotation confirmed | ☐ | ☐ | ☐ |  |
| Vibration — Acceptable | No excessive vibration at blower, condenser fan, or compressor | ☐ | ☐ | ☐ |  |
| Noise — Normal | No abnormal noise: rattling, squealing, or grinding sounds | ☐ | ☐ | ☐ |  |
| Economizer Damper Operation | Damper strokes full open to fully closed; linkage not binding | ☐ | ☐ | ☐ |  |
| OA / RA Damper Position | Minimum OA position verified per TAB / design CFM | ☐ | ☐ | ☐ |  |
| Drain Pan — No Standing Water | Drain pan slopes to drain; no standing water at steady state | ☐ | ☐ | ☐ |  |
| Condensate Trap Primed | Trap primed with water; condensate flowing freely to drain | ☐ | ☐ | ☐ |  |
| Supply Air CFM — Verified | Total CFM measured with balometer or by other approved method | ☐ | ☐ | ☐ |  |
| ESP — Total External Static | Total external static measured and within fan curve limits | ☐ | ☐ | ☐ |  |
| Dirty Filter DP Switch | DP switch trips at correct differential pressure (set per mfr) | ☐ | ☐ | ☐ |  |

📐  SECTION 8 — AIRFLOW MEASUREMENTS

| Parameter | Measured | Unit | Spec / Range | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| Supply Air CFM — Total |  | CFM | Per design / TAB |  |  |
| Return Air CFM — Total |  | CFM | Balanced ±10% |  |  |
| Outside Air CFM — Minimum |  | CFM | Per ASHRAE 62.1 |  |  |
| Supply Duct Static (after fan) |  | in. w.c. | Per design |  |  |
| Return Duct Static (before fan) |  | in. w.c. | Per design |  |  |
| Total External Static Pressure |  | in. w.c. | ≤ Fan rated max |  |  |
| Supply Air Temp (at discharge) |  | °F | Per setpoint |  |  |
| Return Air Temp |  | °F | Record actual |  |  |
| Mixed Air Temp (OA + RA blend) |  | °F | Calculated |  |  |
| Blower RPM (measured) |  | RPM | Per mfr spec |  |  |
| Drive Sheave / Pulley Size |  | inches | Per design |  |  |

📌 NOTE: CFM measurements to be taken with calibrated balometer or Pitot tube traverse. Record actual vs. design CFM. Deviations > 10% require TAB adjustment before job closeout.

🎛️  SECTION 9 — CONTROLS & THERMOSTAT VERIFICATION

| Inspection Item | Criteria / Action | Pass | Fail | N/A | Measured Value / Notes |
| --- | --- | --- | --- | --- | --- |
| Thermostat / DDC Powered | Controller powered and displaying correct room temperature | ☐ | ☐ | ☐ |  |
| Cooling Mode — Functional | Cooling call initiated; compressor and fan confirmed running | ☐ | ☐ | ☐ |  |
| Heating Mode — Functional | Heating call initiated; heat source confirmed operational | ☐ | ☐ | ☐ |  |
| Fan-Only Mode — Functional | Fan-only call runs blower; no heating or cooling active | ☐ | ☐ | ☐ |  |
| Occupied Schedule — Verified | Occupied start/end times confirmed correct for this location | ☐ | ☐ | ☐ |  |
| Unoccupied Setback — Verified | Setup/setback setpoints confirmed active in unoccupied mode | ☐ | ☐ | ☐ |  |
| Setpoint Adjustments Correct | Cooling and heating setpoints match owner's operational needs | ☐ | ☐ | ☐ |  |
| Economizer Control — Verified | Economizer enable/disable conditions tested (if applicable) | ☐ | ☐ | ☐ |  |
| Demand Control Ventilation | CO₂ sensor calibrated; DCV damper modulation verified (if applicable) | ☐ | ☐ | ☐ |  |
| BAS / DDC Communication | All points confirmed communicating with BAS; no faults shown | ☐ | ☐ | ☐ |  |
| Remote Access Tested | Cloud or remote monitoring access verified functional | ☐ | ☐ | ☐ |  |
| Alarm Outputs Tested | Fault relay and/or BAS alarm point confirmed operational | ☐ | ☐ | ☐ |  |

🔥  SECTION 10 — GAS / COMBUSTION CHECKS (If Applicable)

ℹ️ NOTE: Complete this section only for gas-fired equipment (furnaces, RTUs with gas heat, unit heaters). Mark all items N/A for electric-heat or cooling-only equipment.

| Inspection Item | Criteria / Action | Pass | Fail | N/A | Measured Value / Notes |
| --- | --- | --- | --- | --- | --- |
| Gas Type Confirmed | Natural gas or propane — matches equipment configuration | ☐ | ☐ | ☐ |  |
| Inlet Gas Pressure (static) | Measured with manometer before gas valve; within spec | ☐ | ☐ | ☐ |  |
| Inlet Gas Pressure (operating) | Measured under full-fire load; within mfr spec | ☐ | ☐ | ☐ |  |
| Manifold / Burner Pressure | Measured at manifold pressure tap under full fire | ☐ | ☐ | ☐ |  |
| Ignition Sequence — Normal | Igniter glows/sparks; flame established within trial period | ☐ | ☐ | ☐ |  |
| Flame Sensor / Rod — Clean | Flame rod clean; microamp signal within mfr specification | ☐ | ☐ | ☐ |  |
| Flue Gas / Combustion Analysis | CO₂, O₂, CO readings measured and within acceptable range | ☐ | ☐ | ☐ |  |
| Heat Exchanger — No Cracks | Visually inspected; no combustion gas in airstream detected | ☐ | ☐ | ☐ |  |
| Rollout / Overheat Limits | Rollout switch and limit controls reset and operational | ☐ | ☐ | ☐ |  |
| Flue Vent Draft — Verified | Adequate draft; no spillage at draft hood or vent connector | ☐ | ☐ | ☐ |  |

Combustion Analysis Data

| Parameter | Measured | Unit | Spec / Range | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| Inlet Gas Pressure — Static |  | in. w.c. | Per utility spec |  |  |
| Inlet Gas Pressure — Operating |  | in. w.c. | Per mfr spec |  |  |
| Manifold / Burner Pressure |  | in. w.c. | Per mfr spec |  |  |
| Flue CO₂ |  | % | 8–10% (natural gas) |  |  |
| Flue O₂ |  | % | 4–9% |  |  |
| Flue CO (air-free) |  | ppm | < 400 ppm |  |  |
| Stack Temperature |  | °F | Per mfr spec |  |  |
| Net Stack Temperature |  | °F | Stack − OA |  |  |
| Combustion Efficiency |  | % | > 80% |  |  |
| Flame Sensor Current |  | µA | Per mfr spec (≥ 1µA) |  |  |

⚠️  If CO readings exceed 400 ppm air-free, shut down equipment immediately and do not return to service until heat exchanger is inspected and cleared by a qualified technician.

✅  SECTION 11 — POST-STARTUP COMPLETION ITEMS

| Inspection Item | Criteria / Action | Pass | Fail | N/A | Measured Value / Notes |
| --- | --- | --- | --- | --- | --- |
| Manufacturer Startup Form Signed | Completed and signed startup form retained for job file | ☐ | ☐ | ☐ |  |
| Refrigerant Log Completed | All refrigerant quantities, type, and equipment ID recorded | ☐ | ☐ | ☐ |  |
| All Access Panels Reinstalled | All panels, covers, and access doors reinstalled and secured | ☐ | ☐ | ☐ |  |
| System Labels Applied | Refrigerant type label, voltage label, and duct direction arrows | ☐ | ☐ | ☐ |  |
| Spare Parts Left On-Site | Spare filters, belts (if applicable) left with owner/PM | ☐ | ☐ | ☐ |  |
| O&M Manuals Delivered | Equipment operation and maintenance manuals given to owner | ☐ | ☐ | ☐ |  |
| Owner Training Completed | Occupant trained on thermostat, filter changes, and emergency shutoff | ☐ | ☐ | ☐ |  |
| Warranty Card Submitted | Equipment warranty registered with manufacturer | ☐ | ☐ | ☐ |  |
| Punch List — All Items Cleared | All outstanding installation punch list items resolved | ☐ | ☐ | ☐ |  |
| Photos Documented | Before/after photos taken for job file and warranty reference | ☐ | ☐ | ☐ |  |
| Final Inspection — Passed | AHJ / commissioning agent final inspection approved and noted | ☐ | ☐ | ☐ |  |

⚠️  SECTION 12 — DEFICIENCIES & CORRECTIVE ACTIONS

| # | Deficiency Description | Corrective Action Taken | Responsible Party | Date Resolved |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |
| 4 |  |  |  |  |
| 5 |  |  |  |  |
| 6 |  |  |  |  |
| 7 |  |  |  |  |
| 8 |  |  |  |  |

📝  SECTION 13 — FIELD NOTES & OBSERVATIONS

FIELD NOTES & OBSERVATIONS

✍️  SECTION 14 — STARTUP SIGN-OFF & ACCEPTANCE

| Lead Technician | Field Supervisor / PM | Owner / Facility Rep |
| --- | --- | --- |
| Signature: _____________________ | Signature: _____________________ | Signature: _____________________ |
| Printed Name: _____________________ | Printed Name: _____________________ | Printed Name: _____________________ |
| Company: _____________________ | Company: _____________________ | Company: _____________________ |
| Date: _____________________ | Date: _____________________ | Date: _____________________ |

This startup checklist does not replace the manufacturer's startup procedure. Both documents must be completed and retained in the job file.