HVAC EQUIPMENT REPLACEMENT CHECKLIST Complete all sections in sequence. Document existing conditions before removal. Record all measurements before and after replacement.

📋  SECTION 1 — JOB & CUSTOMER INFORMATION

| Work Order #: ________________________ | Service Date: ________________________ |
| --- | --- |
| Customer Name: ________________________ | Customer Phone: ________________________ |
| Service Address: ________________________ | City / State / ZIP: ________________________ |
| Lead Technician: ________________________ | Helper / Assistant: ________________________ |
| Equipment Location: ________________________ | Building / Unit / Floor: ________________________ |
| Reason for Replacement: ________________________ | Failure Mode: ________________________ |
| Permit Required?: ________________________ | Permit #: ________________________ |
| Utility Disconnect Req?: ________________________ | AHJ / Inspector: ________________________ |

🔄  SECTION 2 — EXISTING VS. REPLACEMENT EQUIPMENT DATA

ℹ️ NOTE: Complete the 'Existing' column from the nameplate of the unit being removed before disconnection. Complete the 'Replacement' column from the new unit's nameplate upon arrival.

| Attribute | Existing (Removed) Unit | Replacement Unit |
| --- | --- | --- |
| Equipment Type | ________________________ | ________________________ |
| Manufacturer | ________________________ | ________________________ |
| Model Number | ________________________ | ________________________ |
| Serial Number | ________________________ | ________________________ |
| Nominal Capacity (Tons/MBH) | ________________________ | ________________________ |
| SEER / EER / AFUE Rating | ________________________ | ________________________ |
| Refrigerant Type | ________________________ | ________________________ |
| Refrigerant Charge (lbs) | ________________________ | ________________________ |
| Voltage / Phase / Hz | ________________________ | ________________________ |
| MCA (Min Circuit Amps) | ________________________ | ________________________ |
| MOCP (Max OCPD) | ________________________ | ________________________ |
| Supply CFM — Design | ________________________ | ________________________ |
| Metering Device Type | ________________________ | ________________________ |
| Compressor Type | ________________________ | ________________________ |
| Unit Weight (lbs) | ________________________ | ________________________ |
| Warranty (Parts / Labor) | ________________________ | ________________________ |

📸  SECTION 3 — PRE-REMOVAL DOCUMENTATION & SAFETY

⚠️  Document ALL existing conditions with photos BEFORE removal begins. Failure to do so may void warranty claims and eliminate evidence of pre-existing damage.

| Task / Inspection Item | Criteria / Action Required | Pass | Fail | N/A | Notes / Measurements |
| --- | --- | --- | --- | --- | --- |
| Customer Authorization | Signed work authorization / proposal obtained before work begins | ☐ | ☐ | ☐ |  |
| Before Photos Taken | Photos of existing unit, connections, wiring, and nameplate captured | ☐ | ☐ | ☐ |  |
| Existing Wiring Diagram | Control wiring diagram documented or photo taken before disconnection | ☐ | ☐ | ☐ |  |
| Existing Thermostat Settings | Setpoints, schedule, and program photographed / recorded | ☐ | ☐ | ☐ |  |
| Existing CFM / Airflow Noted | Existing supply and return CFM documented if measurable | ☐ | ☐ | ☐ |  |
| Existing Refrigerant Pressures | Suction and discharge pressures logged before recovery | ☐ | ☐ | ☐ |  |
| Utility Shutoff Confirmed | Gas valve off (if gas); electrical disconnect open and LOTO applied | ☐ | ☐ | ☐ |  |
| Area Protected | Floors, walls, and furniture protected from debris and refrigerant | ☐ | ☐ | ☐ |  |
| Refrigerant Recovery Plan | Recovery machine and certified cylinder available on-site | ☐ | ☐ | ☐ |  |
| Asbestos / Hazmat Check | Existing insulation or materials checked; no hazmat concerns identified | ☐ | ☐ | ☐ |  |
| Load Calculation Reviewed | Manual J / design load verified appropriate for replacement equipment | ☐ | ☐ | ☐ |  |
| Permits Obtained | All required mechanical and electrical permits pulled before work | ☐ | ☐ | ☐ |  |

🔍  SECTION 4 — EXISTING UNIT CONDITION ASSESSMENT

📌 NOTE: Complete this section to document the condition of the existing system. This provides the as-found baseline for warranty, insurance, and liability purposes.

| Task / Inspection Item | Criteria / Action Required | Pass | Fail | N/A | Notes / Measurements |
| --- | --- | --- | --- | --- | --- |
| Coil Condition — Evaporator | Document fouling, corrosion, damage, or blocked fins | ☐ | ☐ | ☐ |  |
| Coil Condition — Condenser | Document fouling, damage, bent fins, or hail damage | ☐ | ☐ | ☐ |  |
| Heat Exchanger (Gas Units) | Inspect for cracks, rust-through, or combustion gas in airstream | ☐ | ☐ | ☐ |  |
| Ductwork Condition | Inspect accessible ducts for leaks, damage, or contamination | ☐ | ☐ | ☐ |  |
| Refrigerant Leak History | Evidence of oil staining, leak repair, or low-charge operation | ☐ | ☐ | ☐ |  |
| Electrical Component Condition | Document burnt wiring, failed contactors, or corroded terminals | ☐ | ☐ | ☐ |  |
| Drain Pan Condition | Check for rust, cracks, biological growth, or overflow damage | ☐ | ☐ | ☐ |  |
| Filter / IAQ Condition | Condition of existing filters; mold or biological growth noted | ☐ | ☐ | ☐ |  |
| Thermostat / Controls | Existing controls compatibility with replacement equipment verified | ☐ | ☐ | ☐ |  |
| Structural / Mounting | Curb, pad, or hanger condition; any repairs needed before install | ☐ | ☐ | ☐ |  |

♻️  SECTION 5 — REFRIGERANT RECOVERY

⚠️  All refrigerant handling must comply with EPA Section 608. Venting refrigerant is a federal violation. Technician must hold valid EPA 608 Universal certification.

| Task / Inspection Item | Criteria / Action Required | Pass | Fail | N/A | Notes / Measurements |
| --- | --- | --- | --- | --- | --- |
| EPA 608 Certification | Technician holds valid EPA 608 Universal certification | ☐ | ☐ | ☐ |  |
| Recovery Machine Verified | Recovery machine calibrated and in proper working condition | ☐ | ☐ | ☐ |  |
| Cylinder Type Correct | Correct recovery cylinder used for refrigerant type; not overfilled | ☐ | ☐ | ☐ |  |
| Full Recovery Completed | System recovered to 0 PSIG (or deep vacuum per EPA standards) | ☐ | ☐ | ☐ |  |
| Refrigerant Type Confirmed | Refrigerant type matches nameplate — no mixed refrigerants | ☐ | ☐ | ☐ |  |
| Recovery Amount Logged | Pounds recovered recorded on EPA refrigerant log | ☐ | ☐ | ☐ |  |
| Cylinder Labeled & Stored | Recovery cylinder labeled with refrigerant type and date; stored safely | ☐ | ☐ | ☐ |  |
| Oil Noted / Trapped | Compressor oil noted; system flushed if contaminated oil detected | ☐ | ☐ | ☐ |  |

Refrigerant Recovery & Charge Log (EPA Required)

| Action | Refrigerant Type | Amount (lbs) | Cylinder / Tank # | Technician & Date |
| --- | --- | --- | --- | --- |
| Recovered from existing unit |  |  |  |  |
| Added to recovery cylinder |  |  |  |  |
| Charged into replacement unit |  |  |  |  |
| Returned / Reclaimed (lbs) |  |  |  |  |
| Net difference (over/under) |  |  |  |  |

🔧  SECTION 7 — EXISTING UNIT REMOVAL

| Task / Inspection Item | Criteria / Action Required | Pass | Fail | N/A | Notes / Measurements |
| --- | --- | --- | --- | --- | --- |
| Electrical Disconnected | All power wiring and control wiring disconnected and labeled | ☐ | ☐ | ☐ |  |
| Refrigerant Lines Capped | Suction and liquid lines capped immediately after disconnection | ☐ | ☐ | ☐ |  |
| Condensate Lines Disconnected | Primary and secondary drain lines disconnected cleanly | ☐ | ☐ | ☐ |  |
| Gas Line Disconnected | Gas supply line capped at stub; union or flexible connector removed | ☐ | ☐ | ☐ |  |
| Duct Connections Removed | Supply and return duct connections detached; openings covered | ☐ | ☐ | ☐ |  |
| Unit Unbolted / Released | Mounting bolts, curb clips, or pad anchors removed | ☐ | ☐ | ☐ |  |
| Unit Removed Without Damage | Existing unit removed without damage to structure, ducts, or wiring | ☐ | ☐ | ☐ |  |
| Old Equipment Disposed | Existing unit disposed per local regulations; refrigerant already recovered | ☐ | ☐ | ☐ |  |
| Mounting Surface Cleaned | Curb, pad, or hanger cleaned; rust, debris, and old sealant removed | ☐ | ☐ | ☐ |  |
| Curb / Pad Condition Checked | Structural condition of curb or pad confirmed acceptable for reuse | ☐ | ☐ | ☐ |  |

🏗️  SECTION 8 — REPLACEMENT UNIT INSTALLATION

📌 NOTE: A new filter-drier is mandatory any time the refrigerant system has been opened to atmosphere. Do not skip this step regardless of the drier's apparent condition.

| Task / Inspection Item | Criteria / Action Required | Pass | Fail | N/A | Notes / Measurements |
| --- | --- | --- | --- | --- | --- |
| New Unit Inspected on Arrival | Unit inspected for shipping damage before installation begins | ☐ | ☐ | ☐ |  |
| Curb / Pad Adapter (if req'd) | Curb adapter or new pad installed and leveled per mfr specs | ☐ | ☐ | ☐ |  |
| Unit Set and Leveled | Unit placed on curb/pad; level verified in two directions | ☐ | ☐ | ☐ |  |
| Unit Anchored | Mounting clips, curb screws, or pad anchors installed and torqued | ☐ | ☐ | ☐ |  |
| Vibration Isolators | Spring or rubber isolators installed per mfr requirements | ☐ | ☐ | ☐ |  |
| Supply / Return Duct Connected | Duct connections made with mastic or foil tape; sealed airtight | ☐ | ☐ | ☐ |  |
| Refrigerant Lines Connected | Existing or new suction and liquid lines connected; no kinks | ☐ | ☐ | ☐ |  |
| New Filter-Drier Installed | New filter-drier installed (mandatory for any system opened to atm.) | ☐ | ☐ | ☐ |  |
| Condensate System Connected | Drain pan, trap, and primary/secondary lines connected and pitched | ☐ | ☐ | ☐ |  |
| Gas Line Connected | New flexible connector installed; gas line leak-tested at connections | ☐ | ☐ | ☐ |  |
| Electrical — Power Wiring | Power wiring connected per NEC; wire gauge, conduit, and terminations | ☐ | ☐ | ☐ |  |
| Electrical — Control Wiring | Control / low-voltage wiring connected per wiring diagram | ☐ | ☐ | ☐ |  |
| Disconnect Verified | Sized per MOCP; within line-of-sight of unit per NEC 440.14 | ☐ | ☐ | ☐ |  |
| All Access Panels Closed | All unit panels secured before energizing for first time | ☐ | ☐ | ☐ |  |

🔬  SECTION 9 — PRESSURE TEST, LEAK CHECK & EVACUATION

| Task / Inspection Item | Criteria / Action Required | Pass | Fail | N/A | Notes / Measurements |
| --- | --- | --- | --- | --- | --- |
| Nitrogen Pressure Test | System pressurized with dry nitrogen to 200–300 PSIG per ASHRAE 15 | ☐ | ☐ | ☐ |  |
| Standing Pressure Test (15 min) | Pressure held for minimum 15 minutes; no drop observed | ☐ | ☐ | ☐ |  |
| Electronic Leak Detection | Electronic leak detector used at all joints, fittings, and welds | ☐ | ☐ | ☐ |  |
| Soap Bubble Check | All field connections verified with leak detection solution | ☐ | ☐ | ☐ |  |
| Leak Test Pressure Recorded | Test pressure and hold time documented in notes column | ☐ | ☐ | ☐ |  |
| Nitrogen Removed | Nitrogen released before charging; system not open to atmosphere | ☐ | ☐ | ☐ |  |
| System Evacuated (Microns) | System pulled to ≤ 500 microns; vacuum held for 30 minutes | ☐ | ☐ | ☐ |  |
| Vacuum Decay Test | Micron gauge monitored 30 min; rise ≤ 100 microns = acceptable | ☐ | ☐ | ☐ |  |
| Micron Level Recorded | Final micron reading before charge break recorded below | ☐ | ☐ | ☐ |  |

Pressure Test & Evacuation Data

| Parameter | Measured | Unit | Spec / Range | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| Nitrogen Test Pressure |  | PSIG | 200 – 300 |  |  |
| Pressure Hold — Start (PSIG) |  | PSIG | Record actual |  |  |
| Pressure Hold — End (PSIG) |  | PSIG | No drop acceptable |  |  |
| Hold Duration |  | Minutes | ≥ 15 |  |  |
| Vacuum — Starting Microns |  | Microns | Record actual |  |  |
| Vacuum — Final Microns (30 min) |  | Microns | ≤ 500 |  |  |
| Vacuum Decay (30 min rise) |  | Microns | ≤ 100 |  |  |

🌡️  SECTION 10 — REFRIGERANT CHARGE & STARTUP MEASUREMENTS

ℹ️ NOTE: Allow minimum 15 minutes of steady-state operation before recording refrigerant measurements. Superheat and subcooling must be within manufacturer specifications before departing.

| Parameter | Measured | Unit | Spec / Range | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| Charge Method Used |  |  | Weigh-in / Subcooling / Superheat |  |  |
| Refrigerant Type |  |  | Per nameplate |  |  |
| Factory Charge (lbs) |  | lbs | Per nameplate |  |  |
| Refrigerant Added / Removed |  | lbs | Record actual |  |  |
| Suction Pressure (steady state) |  | PSIG | Per PT chart |  |  |
| Discharge Pressure (steady state) |  | PSIG | Per PT chart |  |  |
| Suction Line Temp (6" from comp) |  | °F | For superheat calc |  |  |
| Superheat — Calculated |  | °F | Per mfr spec |  |  |
| Liquid Line Temp (at cond outlet) |  | °F | For subcooling calc |  |  |
| Subcooling — Calculated |  | °F | Per mfr spec |  |  |
| OA Dry-Bulb Temperature |  | °F | Record ambient |  |  |
| Return Air Dry-Bulb |  | °F | Record actual |  |  |
| Supply Air Dry-Bulb |  | °F | Record actual |  |  |
| Delta-T (RAT − SAT) |  | °F | 16 – 22 °F typical |  |  |
| Supply Air CFM |  | CFM | Per design / TAB |  |  |
| Total External Static Pressure |  | in. w.c. | ≤ fan rated max |  |  |
| Supply Voltage — L1 to L2 |  | VAC | ±5% nominal |  |  |
| Compressor Amp Draw |  | Amps | ≤ nameplate RLA |  |  |
| Blower Motor Amp Draw |  | Amps | ≤ nameplate FLA |  |  |
| Condenser Fan Amp Draw |  | Amps | ≤ nameplate FLA |  |  |

🎛️  SECTION 11 — CONTROLS & THERMOSTAT CHANGEOVER

| Task / Inspection Item | Criteria / Action Required | Pass | Fail | N/A | Notes / Measurements |
| --- | --- | --- | --- | --- | --- |
| Thermostat Compatibility Verified | New equipment compatible with existing or new thermostat wiring | ☐ | ☐ | ☐ |  |
| New Thermostat Installed | New thermostat installed if required; wired per mfr diagram | ☐ | ☐ | ☐ |  |
| Cooling Mode — Functional | Cooling call tested; compressor and condenser fan confirmed running | ☐ | ☐ | ☐ |  |
| Heating Mode — Functional | Heating call tested; heat source confirmed operational | ☐ | ☐ | ☐ |  |
| Fan-Only Mode — Functional | Fan-only mode tested; no heating or cooling active | ☐ | ☐ | ☐ |  |
| Setpoints Programmed | Cooling and heating setpoints match owner's operational needs | ☐ | ☐ | ☐ |  |
| Schedule Reprogrammed | Occupied / unoccupied schedule re-entered or confirmed correct | ☐ | ☐ | ☐ |  |
| Emergency Heat (Heat Pump) | Emergency heat mode tested and operational if applicable | ☐ | ☐ | ☐ |  |
| Auxiliary Heat (Heat Pump) | Aux heat staging verified functional if applicable | ☐ | ☐ | ☐ |  |
| BAS / DDC Points Updated | BAS point names, equipment ID, and trending updated for new unit | ☐ | ☐ | ☐ |  |
| Filter Alarm / DP Switch Reset | Dirty filter differential pressure switch re-set or re-calibrated | ☐ | ☐ | ☐ |  |
| Controls Labeled | Thermostat, disconnect, and unit control board labeled with unit ID | ☐ | ☐ | ☐ |  |

📷  SECTION 12 — PHOTO & DOCUMENTATION LOG

📌 NOTE: Photos are required for all warranty claims, insurance documentation, and permit inspections. Upload all photos to the job file before closing the work order.

| # | Photo / Doc | When Taken | Description / File Name |
| --- | --- | --- | --- |
| 1 | Existing Unit — Nameplate | Before removal |  |
| 2 | Existing Unit — Overall condition | Before removal |  |
| 3 | Existing Wiring / Control Diagram | Before disconnection |  |
| 4 | Existing Refrigerant Pressures | Before recovery |  |
| 5 | Refrigerant Recovery Cylinder | During recovery |  |
| 6 | Mounting Surface — After removal | After old unit removed |  |
| 7 | New Unit — Nameplate | Before installation |  |
| 8 | New Unit — Set and level | During installation |  |
| 9 | Refrigerant Line Connections | Before pressure test |  |
| 10 | Pressure / Micron Test Gauge | During leak/vac test |  |
| 11 | Electrical Connections | Before energizing |  |
| 12 | Completed Installation | After startup |  |

✅  SECTION 13 — POST-REPLACEMENT COMPLETION ITEMS

| Task / Inspection Item | Criteria / Action Required | Pass | Fail | N/A | Notes / Measurements |
| --- | --- | --- | --- | --- | --- |
| Refrigerant Log Completed | EPA-compliant log: type, lbs recovered, lbs charged, technician cert # | ☐ | ☐ | ☐ |  |
| Manufacturer Startup Form | OEM startup/commissioning form completed and filed | ☐ | ☐ | ☐ |  |
| All Panels / Covers Reinstalled | All unit access panels, covers, and screws reinstalled | ☐ | ☐ | ☐ |  |
| Unit Labels Applied | Refrigerant type, voltage, and service labels applied to unit | ☐ | ☐ | ☐ |  |
| Area Cleaned Up | Job site cleaned; packaging, old parts, and debris removed | ☐ | ☐ | ☐ |  |
| Condensate Drain Primed | Trap primed with water; flow to drain confirmed | ☐ | ☐ | ☐ |  |
| System Run-Time Verified | Unit run minimum 20 minutes steady-state before departing | ☐ | ☐ | ☐ |  |
| Spare Parts / Filters Left | One set of replacement filters left with customer or PM | ☐ | ☐ | ☐ |  |
| O&M Manual Delivered | Equipment operation and maintenance manual given to customer | ☐ | ☐ | ☐ |  |
| Warranty Registration Submitted | Equipment warranty registered with manufacturer | ☐ | ☐ | ☐ |  |
| Owner / Occupant Trained | Customer trained on thermostat, filter replacement, and safety shutoffs | ☐ | ☐ | ☐ |  |
| Permit Final Inspection | AHJ final inspection scheduled or completed (if permit required) | ☐ | ☐ | ☐ |  |
| Job Photos Filed | All required photos uploaded to job file / CRM system | ☐ | ☐ | ☐ |  |
| Invoice / Work Order Completed | All materials, labor, and refrigerant quantities documented on WO | ☐ | ☐ | ☐ |  |

⚠️  SECTION 14 — DEFICIENCIES & CORRECTIVE ACTIONS

| # | Deficiency Description | Corrective Action Taken | Responsible Party | Date Resolved |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |
| 4 |  |  |  |  |
| 5 |  |  |  |  |
| 6 |  |  |  |  |
| 7 |  |  |  |  |

📝  SECTION 15 — FIELD NOTES & OBSERVATIONS

FIELD NOTES & OBSERVATIONS

✍️  SECTION 16 — REPLACEMENT SIGN-OFF & CUSTOMER ACCEPTANCE

| Lead Technician | Field Supervisor / PM | Customer / Owner Rep |
| --- | --- | --- |
| Signature: _____________________ | Signature: _____________________ | Signature: _____________________ |
| Printed Name: _____________________ | Printed Name: _____________________ | Printed Name: _____________________ |
| Company: _____________________ | Company: _____________________ | Company: _____________________ |
| Date: _____________________ | Date: _____________________ | Date: _____________________ |

This checklist must be completed, signed, and filed in the job record. A copy shall be provided to the customer upon request.