📋 SECTION 1 — PROJECT & ASSET INFORMATION

Document Details

| EOL Report Number | _________________________________ |
| --- | --- |
| Date of Assessment | _________________________________ |
| Inspector / Technician | _________________________________ |
| Company / Organization | _________________________________ |
| Work Order Number | _________________________________ |
| Site / Facility Name | _________________________________ |

Equipment Identification

| Equipment Tag / ID | _________________________________ |
| --- | --- |
| Equipment Type | _________________________________ |
| Manufacturer | _________________________________ |
| Model Number | _________________________________ |
| Serial Number | _________________________________ |
| Installation Date | _________________________________ |
| Location / Building | _________________________________ |
| Floor / Zone / AHU # | _________________________________ |

⏱ SECTION 2 — END-OF-LIFE CRITERIA ASSESSMENT

⚠ Complete all applicable criteria. A unit meeting 3 or more FAIL conditions is recommended for replacement.

Age & Service Life Evaluation

| Inspection Item | Pass | Fail | N/A | Notes / Action Required |
| --- | --- | --- | --- | --- |
| Unit has exceeded manufacturer recommended service life (typically 15–20 years) | ☐ | ☐ | ☐ |  |
| Unit is no longer under any active warranty or service contract | ☐ | ☐ | ☐ |  |
| Spare parts / components are discontinued or on extended backorder | ☐ | ☐ | ☐ |  |
| Unit predates current energy efficiency standards (ASHRAE 90.1) | ☐ | ☐ | ☐ |  |
| R-22 or other phased-out refrigerant still in service | ☐ | ☐ | ☐ |  |

Mechanical & Operational Condition

| Inspection Item | Pass | Fail | N/A | Notes / Action Required |
| --- | --- | --- | --- | --- |
| Compressor failure or compressor replacement cost exceeds 50% of unit value | ☐ | ☐ | ☐ |  |
| Heat exchanger cracked, corroded, or failed combustion test | ☐ | ☐ | ☐ |  |
| Evaporator or condenser coil severely fouled / irreparable | ☐ | ☐ | ☐ |  |
| Repeated refrigerant leaks (3+ service calls within 12 months) | ☐ | ☐ | ☐ |  |
| Fan motor failures — repeated or non-repairable | ☐ | ☐ | ☐ |  |
| Economizer or damper actuator non-functional / beyond repair | ☐ | ☐ | ☐ |  |
| Controls / thermostat / BAS integration incompatible or failed | ☐ | ☐ | ☐ |  |
| Structural corrosion on cabinet, frame, or drain pan | ☐ | ☐ | ☐ |  |

Energy & Performance Degradation

| Inspection Item | Pass | Fail | N/A | Notes / Action Required |
| --- | --- | --- | --- | --- |
| Measured SEER/EER/COP below 60% of rated nameplate value | ☐ | ☐ | ☐ |  |
| Supply air temperature deviation exceeds ±5°F from design setpoint | ☐ | ☐ | ☐ |  |
| Airflow measured below 80% of design CFM | ☐ | ☐ | ☐ |  |
| Utility bills show >20% energy increase without occupancy change | ☐ | ☐ | ☐ |  |
| Failed ASHRAE Level 1 energy audit benchmarks | ☐ | ☐ | ☐ |  |

📊 SECTION 3 — PERFORMANCE MEASUREMENTS

Refrigeration Circuit Data

| Parameter | Measured | Unit | Spec / Limit | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| Suction Pressure (Low Side) |  |  |  |  |  |
| Discharge Pressure (High Side) |  |  |  |  |  |
| Superheat at Evaporator Outlet |  |  |  |  |  |
| Subcooling at Condenser Outlet |  |  |  |  |  |
| Refrigerant Charge Weight |  |  |  |  |  |
| Compressor Amp Draw (Actual) |  |  |  |  |  |
| Compressor Amp Draw (Nameplate) |  |  |  |  |  |

Airside Performance Data

| Parameter | Measured | Unit | Spec / Limit | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| Supply Air Temperature |  |  |  |  |  |
| Return Air Temperature |  |  |  |  |  |
| Delta T (Supply vs Return) |  |  |  |  |  |
| Supply Airflow (CFM) |  |  |  |  |  |
| Static Pressure — External |  |  |  |  |  |
| Static Pressure — Supply Duct |  |  |  |  |  |
| Filter Pressure Drop |  |  |  |  |  |

Electrical Data

| Parameter | Measured | Unit | Spec / Limit | Status | Notes |
| --- | --- | --- | --- | --- | --- |
| Supply Voltage (L1-L2) |  |  |  |  |  |
| Supply Voltage (L2-L3) |  |  |  |  |  |
| Supply Voltage (L1-L3) |  |  |  |  |  |
| Voltage Imbalance (%) |  |  |  |  |  |
| Total Unit Amp Draw |  |  |  |  |  |
| Nameplate MCA / MOCP |  |  |  |  |  |
| Power Factor |  |  |  |  |  |

💲 SECTION 4 — REPAIR vs. REPLACEMENT COST ANALYSIS

Cost Summary

| Cost Category | Repair / Refurbish ($) | Replace New Unit ($) |
| --- | --- | --- |
| Immediate Repair / Equipment Cost | $ | $ |
| Labor & Installation | $ | $ |
| Refrigerant / Materials | $ | $ |
| Controls & Integration | $ | $ |
| Estimated Annual Energy Cost | $ | $ |
| Estimated 5-Year Maintenance | $ | $ |
| TOTAL ESTIMATED COST | $ | $ |

Recommendation

Overall Recommendation: ☐ REPAIR — Estimated remaining service life justifies repair cost ☐ REPLACE — Unit has reached end-of-life; replacement recommended ☐ DEFER — Re-evaluate within ________ months Justification / Summary Notes: _______________________________________________________________________________ _______________________________________________________________________________ _______________________________________________________________________________

🔧 SECTION 5 — REPLACEMENT EQUIPMENT SPECIFICATIONS

Required Replacement Specifications

| Replacement Equipment Type | _________________________________ |
| --- | --- |
| Required Cooling Capacity (Tons / BTU) | _________________________________ |
| Required Heating Capacity (BTU/hr) | _________________________________ |
| Minimum Efficiency Rating (SEER / EER / COP) | _________________________________ |
| Refrigerant Type Required | _________________________________ |
| Electrical Supply (V / Ph / Hz) | _________________________________ |
| Physical Dimensions Constraint | _________________________________ |
| Rigging / Access Requirements | _________________________________ |
| Controls / BAS Interface Required | _________________________________ |
| Preferred Manufacturer / Model | _________________________________ |
| Alternative Manufacturer / Model | _________________________________ |
| Target Replacement Date | _________________________________ |
| Estimated Lead Time (Weeks) | _________________________________ |

Scope of Work — Replacement

| Inspection Item | Pass | Fail | N/A | Notes / Action Required |
| --- | --- | --- | --- | --- |
| Decommission and safely recover existing refrigerant (EPA 608) | ☐ | ☐ | ☐ |  |
| Disconnect and remove existing electrical connections | ☐ | ☐ | ☐ |  |
| Remove existing refrigerant piping and drain lines | ☐ | ☐ | ☐ |  |
| Demolish / prepare mounting surface or roof curb | ☐ | ☐ | ☐ |  |
| Install new equipment per manufacturer specifications | ☐ | ☐ | ☐ |  |
| Install new refrigerant line set or re-use if compliant | ☐ | ☐ | ☐ |  |
| Install new condensate drain per code | ☐ | ☐ | ☐ |  |
| Make electrical connections per NEC and local code | ☐ | ☐ | ☐ |  |
| Program / commission controls and BAS points | ☐ | ☐ | ☐ |  |
| Pressure test and charge refrigerant circuit | ☐ | ☐ | ☐ |  |
| Perform start-up and commissioning checklist | ☐ | ☐ | ☐ |  |
| Test and balance airflow per design CFM | ☐ | ☐ | ☐ |  |
| Provide warranty documentation and O&M manuals | ☐ | ☐ | ☐ |  |
| Clean site and dispose of old equipment per regulations | ☐ | ☐ | ☐ |  |

⚙ SECTION 6 — REGULATORY & ENVIRONMENTAL COMPLIANCE

Refrigerant Recovery & Handling

| Inspection Item | Pass | Fail | N/A | Notes / Action Required |
| --- | --- | --- | --- | --- |
| EPA Section 608 certified technician to perform recovery | ☐ | ☐ | ☐ |  |
| Refrigerant recovered using certified recovery equipment | ☐ | ☐ | ☐ |  |
| Recovery cylinder labeled with refrigerant type and weight | ☐ | ☐ | ☐ |  |
| Recovery log completed and retained on file | ☐ | ☐ | ☐ |  |
| Refrigerant disposal / reclaim arranged with certified reclaimer | ☐ | ☐ | ☐ |  |
| Refrigerant type documented for EOL reporting (GWP noted) | ☐ | ☐ | ☐ |  |

Equipment Disposal

| Inspection Item | Pass | Fail | N/A | Notes / Action Required |
| --- | --- | --- | --- | --- |
| Compressor oil drained and disposed of per local regulations | ☐ | ☐ | ☐ |  |
| Capacitors and electrical components disposed of per e-waste rules | ☐ | ☐ | ☐ |  |
| Metal scrap recycled through certified facility | ☐ | ☐ | ☐ |  |
| Foam insulation (if applicable) disposed of per CFC regulations | ☐ | ☐ | ☐ |  |
| Disposal manifest / certificate of destruction obtained | ☐ | ☐ | ☐ |  |
| Disposal records retained for minimum 3 years | ☐ | ☐ | ☐ |  |

Permits & Code Compliance

| Inspection Item | Pass | Fail | N/A | Notes / Action Required |
| --- | --- | --- | --- | --- |
| Mechanical permit pulled prior to replacement work | ☐ | ☐ | ☐ |  |
| Electrical permit pulled prior to replacement work | ☐ | ☐ | ☐ |  |
| Inspection scheduled with AHJ upon installation completion | ☐ | ☐ | ☐ |  |
| Certificate of occupancy / inspection sign-off obtained | ☐ | ☐ | ☐ |  |
| New equipment meets current local energy code (Title 24 / IECC) | ☐ | ☐ | ☐ |  |
| Warranty registration completed with manufacturer | ☐ | ☐ | ☐ |  |

✅ SECTION 7 — SIGN-OFF & AUTHORIZATION

⚠ All signatures required before End-of-Life report is considered complete and filed.

Technician Certification

| Assessing Technician Name: ___________________________ Title: ___________________________ Signature: ______________________ Date: ___________________________ | Lead / Senior Technician (if applicable) Name: ___________________________ Title: ___________________________ Signature: ______________________ Date: ___________________________ |
| --- | --- |

Client / Owner Authorization

| Facility Manager / Owner Representative Name: ___________________________ Title: ___________________________ Signature: ______________________ Date: ___________________________ | Authorizing Executive (if required) Name: ___________________________ Title: ___________________________ Signature: ______________________ Date: ___________________________ |
| --- | --- |

Additional Comments / Conditions

_______________________________________________________________________________ _______________________________________________________________________________ _______________________________________________________________________________ _______________________________________________________________________________